National Iranian Oil Company Safety, Health and Environment Management Building Fire Safety Manual Reviewing Translation; Confirmed by; Publication Date of English Version. Davood Naderi/ Laleh H. Abbasi Training & Performance Measurement Department; Mani Abdollahzadeh Rad/ HSE Manager; September 2018. Responsibility/Subject; Prepared by; Confirmed by; Approved by; Publication date; Descriptions. Name; Mani Abdollahzadeh/ Head of Safety and Firefighting Department/; Siavash Derafshi/ HSE Manager; Ali Kardor/ CEO; August 2016. Position. Document Code NIOC-HSE-SF-WI-019-01 Revision date: August 2, 2016, Revision No.: 1

Contents

1	Introduction	3

2	Goal	4

3	Scope	4

4	Terms and Definitions:	4

4.1	The Standard Fire Test	4

4.2	Alarm	4

4.3	Floor-to-Floor Height and Building Height	4

4.4	Addition	5

4.5	Load-Bearing Members	5

4.6	The Stack Effect	5

4.7	The Fire Alarm Control Panel	5

4.8	Safe Haven	5

4.9	Fire Door	5

4.10	Register	5

4.11	Partition Walls	6

4.12	Fire Compartment	6

4.13	Dropped Ceiling	6

4.14	Sprinkler	6

4.15	Manual Call Point (MCP)	6

4.16	Travel Distance	7

4.17	Shielded Cable	7

4.18	Fire-Resistant Cable	7

4.19	Raised Floor	7

4.20	External Staircase	7

4.21	Escalator	7

4.22	Exit Discharge	7

4.23	Use	8

4.24	Changes	8

4.25	Means of Egress	8

4.26	Positive-Pressure System	8

5	Duties and Responsibilities	8

5.1	Technical Maintenance Services	8

5.2	HSE Department	10

5.3	Employees	11

5.4	Security	12

6 Building Classification by Importance	13

7 Building Technical Certificate	14

8.1	Fire Risk Assessment Process	16

9	Fire Detection, Alarm, and Suppression Systems	17

9.1	Terms and Definitions	18

9.2	Fire Detection, Alarm, and Suppression System Requirements	22

10	Means of Egress and Rescue	26

11	Enhancing Building Fire Safety	27

12	Elevators General Regulations	30

13	The Emergency Response Plan	32

14	Miscellaneous	34

14.1	Using Flammable Fluids	34

14.2	Smoking	34

14.3	Building Electrical Safety	34

15	General Notes on Fire Prevention in Buildings	37

16	References	37

17	Appendices	37

Appendix 1. Directive on the Prohibition of Smoking	38

# 1	Introduction

Neglecting building safety principles results in several devastating incidents every year. According to the Municipality of Tehran, 21,558 cases of fire were reported in Tehran in 2014, indicating a 4.34% rise compared to the year before.

Given the fact that fire is one of the major hazards in buildings, it is inevitable to pay particular attention to fire-safety and consider it in design, construction and utilization. Devices and systems with a preventive and reactive approach can play an important role in reducing the risks and consequences using the fire warning and suppression equipment. In this regard, it is essential to provide a robust fire-safety framework by considering the scientific and technical building design principles, including:

- Making the necessary arrangements in the design and construction of the buildings to prevent fire;

- Providing fire detection, warning, alert, control, and suppression systems in the building;

- Preventing the spread of fire and smoke in the building;

- Foreseeing exits for the safe and timely egress of people from buildings and their transfer to the safe places;

In this regard, the safety and fire department of the HSE management of the National Iranian Oil Company (NIOC) has developed the “Building Fire Safety Manual” based on various resources. The document provides a set of minimum requirements and safety principles for fire safety in buildings.

It is obvious that this manual does not include all requirements and does not undermine other safety requirements, regulations, and instructions.

# 2	Goal

This document was prepared with the following objectives:

- Establishing the minimum fire-safety requirements in buildings;

- Controlling the risks and consequences;

- Improving emergency response readiness;

- Reducing casualties and damages.

# 3	Scope

All buildings owned or rented by the NIOC and its subsidiaries

# 4	Terms and Definitions:

## 4.1	The Standard Fire Test

The standard test (or tests) serving to evaluate the resistance and behavior of materials, products, and construction members and components against fire

## 4.2	Alarm

A warning device that is activated by the fire warning system in the event of a hazard to warn the residents using a powerful sound

## 4.3	Floor-to-Floor Height and Building Height

The floor-to-floor height is the vertical distance between the finished top of two successive floors in a building. The height of the top building floor is considered to be the vertical distance between the top of that finished floor and the midpoint of the roof.

However, the height of building is defined as the total height of the building or the vertical distance between the average, natural ground level and the midpoint of the roof.

## 4.4	Addition

Any construction that adds to the surface or volume of a building

## 4.5	Load-Bearing Members

Those components of the building that transfer that dead and live loads of the building to the foundation

## 4.6	The Stack Effect

The vertical flow of air inside the buildings as a result of the difference between indoor and outdoor temperatures

## 4.7	The Fire Alarm Control Panel

A device that monitors every component of the fire alarm system in the buildings (or any specified location) and informs any case of possible fire through activating the alarms if it detects any sign of smoke, fire, or damage

## 4.8	Safe Haven

A safe space that serves as a temporary shelter in the event of a fire

An area of 0.28 m2 must be considered for each individual.

## 4.9	Fire Door

A door that has passed the “standard fire test” and is proven to satisfy fire resistance and protection requirements for a given period of time

## 4.10	Register

Ceiling or wall-mounted grilles that blow fresh air coming from an air handler, cooler, or a positive pressure fan into the room

## 4.11	Partition Walls

Separators made of wood, PVC, or light construction materials that serve for temporary or permanent partitioning

## 4.12	Fire Compartment

A confined space within the building that is separated from other areas by fire-resistant implements such as walls and doors

## 4.13	Dropped Ceiling

A light-weight second ceiling that is hung from the main ceiling and provides space for piping, facility ducts, and cables in addition to reducing the ceiling height.

## 4.14	Sprinkler

The water sprinkler is a system composed of tanks, pumps, pipes, valves, and fixed nozzles.

Nozzles are often equipped with a heat-sensitive [electrical/mechanical] fuse which activates water sprinkler in the event of a fire, and provides a cool pass for residents to escape through, in addition to extinguishing the fire.

## 4.15	Manual Call Point (MCP)

Fast-activating Manual Call Points (MCP) are installed in the hallways, near exit doors, the entrances, assembly areas, or other places with a high risk of accidents or fire. By pressing the glass, a signal is transmitted to the fire alarm control panel which initiates the programmed operations in the fire alarm system.

## 4.16	Travel Distance

The distance that a person needs to travel to reach one point from another

## 4.17	Shielded Cable

A type of cable that is equipped with a special metal shield that prevents electromagnetic interference,

## 4.18	Fire-Resistant Cable

Cables with a suitable coating to withstand fire at a certain temperature for at least two hours without being damaged or losing performance

## 4.19	Raised Floor

An elevated flooring system that provides space for electrical or mechanical facilities below the surface and is often used in constructions such as control or communication rooms, data centers, or theatrical stages

The raised floor can be 50 to 1200 mm high.

## 4.20	External Staircase

A staircase that has more than one open side

## 4.21	Escalator

A stairway that is moved by means of mechanical devices

An escalator is not considered a part of the means of egress.

## 4.22	Exit Discharge

The portion of the means of egress that is between the building exit and the public way

## 4.23	Use

The use of a building is the purpose for which it, or a part of it, is used or will be used.

## 4.24	Changes

Any changes in the building, its exits, or mechanical and electrical facilities that are not part of an addition project

## 4.25	Means of Egress

A continuous, unobstructed path to reach an open area or public way from any point within the building

## 4.26	Positive-Pressure System

A system that supplies fresh air at a higher pressure, with respect to the surroundings (specified pressure), to block smoke from entering a particular area

# 5	Duties and Responsibilities

According to the organizational structure and job descriptions, the responsibility for securing the building and maintaining its safety shall be defined as follows in every company/organization.

It must be noted that the duties and responsibilities of the named authorities are not limited to what is pointed out here and may differ based on the type of activities in the company and the circumstances.

## 5.1	Technical Maintenance Services unit

The unit in charge of the upkeep of the building with the following responsibilities:

5.1.1. All buildings are required to have a specific unit assigned to the job of repair and maintenance. This unit will be responsible for the maintenance, repair, regular and planned inspection, and monitoring of the building.

5.1.2. The technical maintenance unit is responsible for solving the issues, maintaining compliance with safety and technical regulations, as well as cooperation with all concerned units in the building.

It is obvious that any changes in the use of the building must be carried out with the coordination, approval and supervision of this unit, in compliance with the change management guidelines of the NIOC (MOC-NIOC-HSE-SF-GU-007-00).

5.1.3. If new facilities are being constructed, or changes are made to the current ones, the HSE department must be informed in writing by the technical maintenance unit.

5.1.4. Re-arranging partitions or making any changes in the building or office or installing new doors must be carried out through informing the HSE department in advance through the technical maintenance unit.

5.1.5. Any new installations, changes, or displacement of electrical facilities must be carried out in coordination with this unit by the building’s own electrical maintenance unit.

5.1.6. The unit/department must prepare an emergency response manual and conduct drills in cooperation with the HSE department to evaluate the awareness and performance of the employees in emergencies.

5.1.7. The technical maintenance unit is also responsible for monitoring fire warning and suppression systems including fire pumps, fire hose cabinets, fire extinguishers, fire detection and alarm systems, etc. to ensure their correct function in the office areas. In NIOC subsidiaries where the technical services unit does not include a safety and fire department, this must be carried out by the HSE department.

5.1.8. The unit is required to install first-aid cabinets in the buildings and supply them. In addition, they are required to provide the employees with the training required to use the equipment.

5.1.9. Before any earthworks, destroying walls or trenching, it is essential to contact the related authorities to be informed of any buried cables or infrastructures and obtain the required permits (cold work permits and the excavation certification).

5.1.10. To compensate for the potential damages from incidents, it is essential to have insurance coverage for all buildings in coordination with the HSE department.

## 5.2	HSE Department

This applies to the HSE units/departments of the subsidiaries and associates. In addition, in case of the buildings located in Tehran and administered by the department of logistics of NIOC, the following responsibilities apply to the HSE/safety and fire department of the technical service unit.

5.2.1. Controlling and supervising the training and implementation of emergency response manuals in all buildings.

Fire safety regulations and the emergency response manual must be provided to the personnel and explained to them comprehensively and clearly.

5.2.2. Making sure that the emergency drills with various potential scenarios are conducted according to the plans to review, analyze, and reveal the weaknesses.

5.2.3. The HSE department is responsible for inspecting the buildings, reporting the results to the technical service unit, and following up on the progress. It is also essential to identify and resolve the safety issues and defects before occupancy.

5.2.4. The approval of the HSE department is necessary for the followings during the building design stage:

5.2.4.1. All the necessary fire warning and suppression equipment, and safety instruments required for protecting the employees, facilities, and the buildings must be planned in the initial design.

5.2.4.2. The equipment used to suppress fire in public facilities and areas must be appropriate for local conditions and in compliance with standards, national regulations, and the requirements of the oil industry.

5.2.4.3. The risk of fire and explosion must be assessed considering the significance of industrial and non-industrial facilities in terms of the fire load and standard fire-safety; and protection systems must be designed incorporating cutting-edge technologies.

5.2.5. Any displacement of the fire suppression equipment is prohibited unless authorized by the HSE department.

5.2.6. The Safety and Firefighting Equipment Layout plan, showing emergency exits and muster points must be prepared and installed in suitable places within the building.

5.2.7. In cooperation with the training department, the HSE department is required to hold safety and fire suppression training courses for the employees to expand their knowledge in this regard.

## 5.3	Employees

The employees working in the units and buildings are required to conform to the following measures:

5.3.1. In case of leaving the workplace or office for more than one hour, the users are required to turn all electrical appliances off from the main outlet.

5.3.2. In addition to reporting to the related departments/organizations in case of fire or smelling smoke in the building, all employees are required to proceed to suppress the fire using extinguishers or other equipment if possible; otherwise, they must leave the place immediately through the main or emergency means of egress.

5.3.3. When entering or exiting the workplace after office hours, all employees are required to enlist their names in addition to the date and time of entry/exit, according to security instructions.

5.3.4. For safety and energy-saving reasons, the employees must make sure that the windows are closed when air conditioning is on.

5.3.5. In buildings with a central air conditioning system, the system shall be turned on or off only by the maintenance workers.

5.3.6. The employees are required to report any hazard or defect in the electrical equipment to the maintenance department of the building immediately.

5.3.7. The employees must receive general fire safety and suppression training in order to learn how to use the fire suppression equipment.

5.3.8. After using fire extinguishers, it must be reported to the HSE department to replace them with new ones.

## 5.4	Security

As specified in security instructions, it is necessary to carry out the following measures:

5.4.1. The entry and exit information of the employees and visitors to the office buildings must be carefully recorded, especially after office hours.

5.4.2. The keys to all the rooms and offices must be kept by the security/maintenance department in a locked cabinet for emergency use. It must be noted that any use of these keys must be reported.

5.4.3. It is essential that the security employees are trained in advance to inform the residents as instructed and respond to emergencies (such as fire, earthquake, or other unforeseen incidents) using the available equipment before firefighters and rescue teams arrive at the scene.

5.4.4. It is necessary that the security employees of the building patrol all hallways and floors according to standard operating procedures, investigate any suspicious circumstances, and report it if necessary.

5.4.5. Security officers are required to make sure the doors are locked after the office hours.

5.4.6. The security department is required to control emergency exits and report potential issues to make sure they can be safely used.

5.4.7. In emergencies, security personnel must cooperate with the HSE department and prevent spectators from crowding.

5.4.8. Planning and installing surveillance cameras in the important office buildings.

# 6 Building Classification by Importance

Based on the usage, the number of residents or workers, the value of assets they house, the constructed area, and the number of floors, buildings are classified into five groups:

	Group 1: Particularly important buildings;

	Group 2: Very important buildings;

	Group 3: Important buildings;

	Group 4: Slightly-important buildings;

	Group 5: Buildings of low importance.

More complete definitions can be found in Clause 21.1.6 (building classification) of Chapter 21 (civil defense) of the National Construction Regulations.

# 7 Building Technical Certificate

According to Clause 13.1.2 of Chapter 13 of the general safety regulations, the first step in controlling and preventing incidents is to evaluate the current building status, making it essential to prepare a technical certificate for the building.

7.1. The definition of a technical certificate: It is a collection of essential information showing the general status of the building.

The technical certificate must be prepared by the Technical Maintenance and Safety and Fire departments and revised at least annually.

7.1.1. If any changes are made to the building, the building administrators must review and correct the technical certificates.

7.1.2. According to the National Construction Regulations, the technical building certificate must cover:

	The general building specifications;

	Fire alarm and suppression equipment;

	Electrical and mechanical facilities;

	Fire resistance;

	Elevators;

	Emergency response;

	Medical support, first aid, and rescue.

Other complementary information may be required in particular cases and must be added at the discretion of the respective maintenance and safety departments.

To evaluate the building status, it is essential to prepare a checklist based on which the building will be inspected by the technical maintenance and safety departments as scheduled to identify issues and correct them.

Smoke and Heat Exhaust

Air Inlet

Walls and the Ceiling Structure

Openings Status

Spatial Geometry (building interior and exterior design)

Materials composition

8	Fire Risk Assessment

During the design, construction, or utilization of the building, the risk of fire and its potential consequences must be predicted and appropriate arrangements must be made. The degree of fire hazard in a building determines how important a risk the residents are exposed to. The degree of hazard is determined based on the fixed and moving tooling and constructions in the building, their fire spread, the type of indoor activities, the building fire load, etc.

The main goals of fire risk assessment are:

 Securing the residents and allowing them to exit safely in the event of a fire;

 Limiting damages to the assets including the structure and the equipment;

 Accelerating the response and enhancing the efficiency of fire suppression and rescue operations;

Upholding the organizational reputation

Limiting the damage is possible through familiarity with the fire behavior and safe building design.

The priority is to limit the fire to its origin and preventing its spread to other floors or buildings.

The figure below illustrates factors affecting the fire behavior and their relationship.

Fire Behavior

Temperature

Fire Load

Type of Materials

Time

Amount of Materials

## 8.1	Fire Risk Assessment Process

Generally speaking, fire risk assessment can be broken down into three steps:

8.1.1. Identifying the Hazards:

In general, fire hazards in buildings are classified into internal and external hazards as follow:

8.1.1.1.	Internal Hazards: Internal fire hazards are identified based on the followings:

 Construction materials;

 The type of fixed and moving structures in the building;

 The building usage;

 Routine and occasional activities in the building.

8.1.1.2.	External Hazards: These hazards are classified into two general groups:

- Activities near the building;

- The natural surroundings.

8.1.2. Risk Analysis: The risk and severity of a potential fire must be calculated realistically based on the identified hazards.

In fire risk assessment, often, two scenarios are investigated carefully:

 The fire behavior scenario;

 The human behavior scenario.

3.1.8. Proposing solutions and fire control plans: A corrective action plan for fire control and emergency readiness will be developed based on the fire risk analysis results.

All interactions are also required to be taken into account as comprehensively as possible in planning the safety program and the corrective and preventive actions, this includes:

The start of the fire;

 The spread of fire and its emissions;

 The layout, reinforcement, and structural stability;

 Fire detection, warning, and suppression;

 The individual behavior and emergency evacuation;

 Fire suppression by the fire department

# 9	Fire Detection, Alarm, and Suppression Systems

To detect fire and limit its consequences, it is essential to equip the buildings with fire detection, alarm, and suppression systems according to the regulations and requirements.

Notable standards for designing and implementing fire alarm systems are:

- NFPA 72

- BS‐EN 54

## 9.1	Terms and Definitions

9.1.1	The Fire Zone: A zone or area - consisted of one or more sections - which is specified based on the usage of the sections and their extent and is equipped with fire alarm devices such as detectors, call points, etc. and is defined in the fire control panel separately.

9.1.2. Fire Detection and Alarm System: A system of detectors, sirens, visual alarms, and various modules, that detects a fire in the shortest time possible and, in addition to warning the residents and workers about the danger, can activate ventilation, automated suppression, and elevator control, open/close fire and smoke dampers, etc.

9.1.3. Automatic Alarm System: In addition to the call points, siren, and visual alarms, this system incorporates automatic smoke, heat, and flame detectors and a central control panel that allows the activation of the fire alarm both manually and automatically in the floor, section, or even the area where the fire has started.

9.1.4. Addressable Alarm System: A unique address is assigned to every element composing this system, including detectors, call points, bells, and input and output modules, based on which the control panel identifies the location of the incident, showing its status and descriptions on the display to use and direct the personnel quickly.

9.1.5. Manual Alarm System: A number of call points, sirens, and visual alarms are installed at different locations, and connected to the power supply in a common or separate area.

Normally, the call points are open, not allowing current into the circuit.

However, if a call point is activated, electricity runs through the circuit, triggering all sirens in the area.

The call points in separate areas only trigger alarms in their respective area.

9.1.6. Optical Beam Detectors: The beam detector is composed of a transmitter that projects a beam and a receiver (mirror) that receives their reflection. When smoke cuts the beam’s path fire detection is initiated.

These detectors can cover a maximum area of 100 in 15 m2.

9.1.7. Combination Detectors: A combination detector reacts to smoke and heat using a programmed fire detection algorithm or model which improves the speed of response in addition to reducing false alarms.

9.1.8.	Point Detectors: This type of detectors is designed to be placed at a certain point and is available in smoke, thermal, and gas (carbon monoxide, toxic gases, and combustible gases) detector types.

9.1.9. Rate-of-Rise Detectors: These detectors react to a certain rises in the ambient temperature in a given time interval. They are also available in fixed-temperature types.

9.1.10. Fixed-Temperature Heat Detectors: This detector is activated at a certain temperature (for example 58 °C).

9.1.11. Linear Smoke Detectors: In these detectors, the process of fire detection is carried out along a straight line. Examples of this type of detector include optical beam detectors, heat-sensitive cables, and their latest generation which incorporates optical fibers and laser.

9.1.12.	Point Smoke Detectors: These detectors are sensitive to smoke.

Smoke detectors are classified into ionization and optical types.

The ionization smoke detectors are sensitive to small, sub-micron particulates.

Meanwhile, based on their operating mechanism, the optical smoke detectors are classified into direct and indirect types, with the latter being more popular due to its higher accuracy, which leads to fewer false alarms.

9.1.13. Flame Detectors: The formation of hot gases from a flame is associated with infrared, visible, and ultraviolet radiations.

Drawing on this characteristic, flame detectors are designed to react to infrared and ultraviolet radiations.

9.1.14. Gas Detectors: Using infrared or electrochemical sensors, this type of detector identifies gas emissions and alerts the control panel if the threshold is exceeded.

9.1.15. Local Detectors: This type of detectors is installed in smaller and less-populated areas if needed and serves for fire detection and warning.

9.1.16. Air-Sampling Detectors: Using tubes that are attached to a central unit, this type of detector sucks in the air with the help of a pump or the ventilation air flow and analyzes it.

9.1.17. Detector Coverage: The area covered by a single detector for the detection of toxic or explosive gas leaks.

9.1.18. Interface: In fire alarm systems, accessories known as “Interfaces” or “Modules” are used to connect and control auxiliary systems in the area, such as the elevator, fire pumps, positive pressure fans, exhaust fans, and other equipment that are needed to be commanded or turned on/off by the fire alarm system.

9.1.19. Visual Fire Alarms: A type of alarm that informs the residents of an imminent danger with the help of visual signals such as warning lights or signs.

9.1.20. Fire Extinguishers: Fire extinguishers are used in the initial stages of fire to suppress it locally. These devices are available in various sizes and in hand-held and wheeled types.

Types of fire extinguishers include:

- Water extinguishers;

- Foam extinguishers;

- Dry powder extinguishers;

- Carbon Dioxide (CO2) extinguishers.

All office buildings are required to have safety and firefighting equipment layout plans and safety signs installed at suitable locations.

## 9.2	Fire Detection, Alarm, and Suppression System Requirements

The design, implementation, and any changes to the fire detection and alarm systems must be in compliance with the regulations, instructions, codes, and trusted national and international standards approved by the NIOC, including ISIRI, NFPA, BS-EN, and IPS.

9.2.1. All office buildings, and training, cultural, or accommodation facilities of any size must be equipped with an addressable and automatic fire detection and alarm system.

9.2.2. The devices and equipment incorporated into the fire detection, alarm, and suppression system are required to be approved by the HSE department of the company or the respective organization.

9.2.3. The main parts of the fire detection and alarm system are:

- Detector;

- Siren;

Call-point;

- Central control panel;

- Interface.

9.2.4. All main parts of the fire detection and alarm system must be approved and certified by an eligible authority and tested according to NFPA or BS-EN54 standards.

9.2.5. NIOC accepts the following international certifications for fire detection and alarm system components:

AFNOR, BRI (LPCB), BSI, VDS, FM, UL

9.2.6. The components incorporated into a system must be compatible in the following aspects:

	All components must be products of the same manufacturer;

	In case the components are not produced by the same manufacturer, it is essential to provide authentic technical documents verifying that the components are compatible.

	Otherwise, the compatibility of the components must be verified by eligible authorities.

9.2.7. The cables used in the electrical wiring of the fire detection and alarm system must conform to national Iranian standards or trusted international ones.

9.2.8. The system must incorporate quality, standard alarm lights.

9.2.9. All buildings must be equipped with fire extinguishers suitable for the type of combustibles in the area.

9.2.10. Dry riser systems must be implemented adjacent to emergency exits or fire escapes on every floor of multi-story office buildings

.

9.2.11. All office buildings must be equipped with fire cabinets, including hose reels, nozzles, valves, and fittings.

9.2.12. It is necessary the firefighting water pumps in the buildings are connected to an emergency power supply in addition to the mains.

9.2.13. All buildings, in which the vertical distance between the floor of their top, occupied flat and the level accessible for firefighting trucks is more than 23 meters, are required to be equipped with a sprinkler system and verified by the HSE department.

9.2.14. Sprinkler fire suppression systems are mandatory for medical buildings.

9.2.15. Fire detection, alarm, and suppression systems must be inspected and tested periodically in the presence of the representative of the safety and fire department.

9.2.16. The smoke and fire alarm system must be equipped with batteries that can power the system for 24 hours of normal function and 5 minutes of the alarm.

9.2.17. The main fire detection and alarm control panel must be installed in either the security office or maintenance office.

9.2.18. All five-story, and taller (considering the above-ground height), residential buildings must be equipped with both automatic and manual fire detection and alarm systems.

9.2.19. In the buildings with required installation of automatic fire detection and alarm systems, manual fire detection and alarm systems are also necessary.

9.2.20. Computer labs, data centers, and archives may need to be equipped with total floating fire detection, alarm, and suppression systems, at the discretion of the eligible authorities.

9.2.21. All hallways in medical care centers, all units in hospitals, rehabilitation centers, clinics, nurseries, and kindergartens must be equipped with automatic fire detection and alarm systems.

9.2.22. Automatic fire detection and alarm systems must be installed in warehouses unless the safety and fire unit verifies that the storage is incombustible and low-risk.

9.2.23. The minimum diameter or cross-sectional area of the conductors used in the fire detection and alarm system must be in compliance with the manufacturer’s instructions.

The wires shall not have a minimum cross-section of below 1 mm2.

9.2.24. The cables of the fire detection, alarm, and suppression system must be laid at a distance of at least 30 cm from other cables.

9.2.25. Use of non-standard fittings and joints (for example, adhesive tapes) is strictly forbidden in the components of the fire detection and alarm system.

9.2.26. When connecting a conductor to a terminal, it is necessary to use cable and wire terminations and secure the connection.

9.2.27. It is necessary to ground the central alarm panel using a wire with an electrical resistance of below 5 ohms.

9.2.28. The cables of the fire detection and alarm system laid outdoors, e.g. the parking lot, must run inside metal tubes.

9.2.29. In all buildings, fire-resistant cables must be used for the fire alarm sirens.

It must be noted that in some places, at the discretion and with the approval of the engineering, safety and fire departments, the entire automatic fire detection, alarm, and suppression system must be wired using fire-resistant cables.

9.2.30. The fire detection, alarm, and suppression system is required to be wired using identical cables that are distinct from other cables; and it is prohibited to use cables of different colors for this purpose.

9.2.31. A lightning arrester system must be installed for the outdoor, overhead cables of the fire detection and alarm system before it is connected to the first fire alarm element.

If more than 600 meters of cables run outdoor, a lightning arrester is required to be installed at 600-meter intervals.

In addition, the central control panel of the fire detection and alarm system must be powered by a lightning-protected electrical supply.

9.2.32. All power-supply circuits, including batters and mains, must be equipped with fuses of suitable rating.

Fuses with 20 A, 40 V ratings or higher must be shielded and come with a cap.

9.2.33. According to the manufacturer’s requirements, the addressable fire detection and alarm systems must be wired using shielded and grounded cables.

# 10	Means of Egress and Rescue

Emergency exit and rescue routes are important requirements for building safety and reducing the risks. These routes allow for the fast and reliable evacuation of the personnel and residents and provide access for the rescue and firefighting teams, and their equipment and devices. A means of egress is a continuous, unobstructed path stretching from any point within the building to a public way (alley or street). The means of egress is composed of three separate, distinct parts including the exit access and the exit discharge. The elevators are not considered parts of the means of egress. The design and implementation must provide safe and easy access to a safe area inside or outside the building in the event of a fire.

In this regard, it is necessary that:

10.1. Adequate means of egress of sufficient capacity are planned throughout the building, providing a smooth and easy access to a safe area.

10.2. The evacuation path is illuminated adequately and all exits are marked with proper, distinctive signs.

10.3. It is required that the necessary measures are taken to prevent the flame and smoke from spreading to the exit paths in a manner that is appropriate in relation to the usage, size and height of the building.

The special requirements and regulations in this regard can be found in Chapter 3 of the National Construction Regulations.

# 11	Enhancing Building Fire Safety

It is essential that, in addition to planning for the necessary fire safety arrangements, the building is designed and constructed to withstand fire for long enough and not to allow the spread of fire to adjacent areas and buildings. In this regard, it is of utmost importance to conform to the basic following requirements in the design and construction of the buildings.

11.1. The necessary arrangements must be made to prevent the spread of fire inside the building through internal wall coverings and finishes. Accordingly, it is important to:

11.1.1. use incombustible or fire-retardant materials.

11.1.2. select wall coverings that hinder the spread of flames over the surface and produce a limited amount of heat when burning.

11.1.3. plan the interior layout adequately considering the use and size of the building to prevent the spread of fire with the help of fire-resistant structures.

11.2. Instructions for wall finishes and interior design

11.2.1. Combustible materials (such as carpets, floorings, etc.) shall not be used in hallways, fire escapes, entrances to units, or on the ceiling.

11.2.2. Combustible materials shall not be used to decorate or in the wall finish in assembly areas, cinemas, and emergency access routes in any building.

11.3. Heating system regulations

11.3.1. All buildings must have central heating systems. The use of space heaters with an open flame is prohibited.

11.3.2. The gas pipework of the building must be approved by the gas department.

11.3.3. For each branch of the gas pipework, except for illumination, a separate chimney must be considered that runs up to 80 cm above the roof level and is terminated with proper caps.

11.3.4. If possible, the kitchens of restaurants must be located under an open area; or if it is located at the basement of a building, it should be adjacent to an open area, and not under the assembly room.

11.4. Boiler room requirements

11.4.1. Whenever possible, the boiler room must be planned outside the building. Otherwise, it must be located adjacent to an open space or have a window facing the open area.

11.4.2. The boiler room of the facilities shall not be adjacent to an elevator pit, staircase, or an assembly room. Otherwise, they must be separated by a fire-resistant wall.

11.4.3. Separate ducts are to be considered for facility pipes, electrical cables, and chimneys.

11.4.4. A metal door and clear space through the doorway must be considered for the boiler room.

11.4.5. A suitable ventilation system is to be planned in proportion to the size of the boiler room.

11.4.6. All pressurized vessels must be equipped with safety valves.

11.4.7. Surface-mounted electrical wiring is prohibited unless the cables run through a special tube.

11.4.8. Special, protected lights must be used.

11.4.9. The boiler room of the facility must be equipped with the fire detection, alarm, and suppression system and safety equipment.

11.4.10. A floor-cleaning machine must be available in the boiler room.

11.4.11. At least one-third of the space in the boiler room must remain empty.

11.4.12. All torches are required to be equipped with a thermocouple control valve.

11.5. Considerations on Stone and Glass Exterior Wall Systems

11.5.1. Tempered glass is required to be used in curtain walls.

11.5.2. A minimum width of 1 m fire-resistant materials must be used at the intersection between the separating walls and the glass curtain wall to prevent the spread of fire through the back of the curtain wall.

11.5.3. The glass thickness must be selected in proportion to its dimension and a 2 cm gap must be considered at every six meters in height.

11.5.4. The stones must be placed and secured over an angle beam at every three meters in height.

11.5.5. The glass frames must be fixed and secured.

11.5.6. The stone fasteners over the caps must be fastened tightly.

11.5.7. If the building is, entirely or partially, constructed over a steel frame, it is essential to specify the required fire resistance based on Chapter 3 of the National Construction Regulations. The details of reinforcement, including the type and thickness of materials, linings, and products and implementation standards must be noted in the construction drawings. The fire resistance design calculations along with the standard quality and products safety documents, the method of practice, and construction drawings must be approved by the Firefighting and Urban Safety Services Organization.

11.5.8. In case of

constructing the building using dry walls entirely or partially (lobby separating walls, elevators, exit access walls, etc.) instead of materials that, according to Chapter 3 of the National Construction Regulations, are required to be structurally resistant to fire, it must be verified by trusted laboratories that the incorporated materials meet the required resistance.

Special requirements and regulations in this regard can be found in detail in Chapter 3 of the National Construction Regulations (Building Fire Protection), the Architectural Safety Regulations (Tehran Firefighting and Urban Safety Services Organization), and the regulations and instructions of the Tehran Firefighting and Urban Safety Services Organization.

# 12	Elevators General Regulations

12.1. The elevators must be located outside the staircase.

12.2. The elevator pit must reach down to the building’s foundation.

12.3. The elevator pit must have an effective area of at least 150 cm in 150 cm.

12.4. The access door to the elevator pit shall be located in the boiler room.

12.5. A separate machine room, with a 60 × 80 cm2 access hatch below the room that opens outward, must be allocated to the elevator.

12.6. Any opening, aperture, or window to the elevator pit in addition to the access hatch is prohibited.

12.7. Conforming to all elevator installation standards (pertained to the cabin, the motor, the shaft, etc.) and having the verification of the Iran quality inspection standard for that matter are mandatory.

12.8. Annual inspection by eligible authorities, inspection of the industrial equipment and certification of the technical and safety integrity of the elevators by the Department of Building Maintenance and Technical Services is necessary.

12.9. The elevators in office buildings must be inspected thoroughly and periodically by technicians from eligible units. This includes the inspection of the parachute system, micro-switches, the emergency telephone, safety relay, illumination, the function of the safety circuit, and other items noted in the inspection checklist. Any defects or faults that were found must be resolved immediately.

12.10. Facility piping (e.g. hot or cold water, chimney, gas pipes, or electrical cables) that is not a part of the elevator’s own equipment shall not run through the elevator pit.

12.11. A switch lock must be installed on the elevator’s machine room access hatch.

12.12. A 2×2 cm2 mesh grille must be installed on the windows and apertures of the machine room.

12.13. The door of the elevator cabin must be equipped with a hands-free telephone, emergency alarm, ventilation, and 12 W illumination powered by a battery and an automatic charging relay.

12.14. Lateral walls in the elevator pit must be fire-resistant, self-supporting, and without apertures.

12.15. It is essential that the steel frame of the elevator pit, the cabin, the frame, and all other parts of the elevator are connected to an earthing or grounding system with a maximum electrical resistance of 50 ohms.

12.16. Signs warning about using the elevator in the event of a fire must be installed.

The requirements in this regard can be found in Chapter 3 of the National Construction Regulations (Building Fire Protection), Clause 3.1.24, specific regulations for the elevator.

## 13	The Emergency Response Plan

The companies must develop operating manuals to identify, prepare for, and respond to emergencies through a systematic study and analysis. Regularly-updated records must be kept from the identified emergencies to guarantee an effective response to the emergencies. To make sure that the companies are prepared for an emergency, it is essential to undertake planned drills suitable for the risks in the environment to reveal the weaknesses and adopt corrective measures accordingly.

13.1. The buildings must have a codified emergency and crisis response plan.

13.2. These plans must be developed by the maintenance and technical unit

.

of the building under the supervision of HSE authorities services

13.3. The crisis response plan must take into account the concerns of other units based in the building.

13.4. The crisis response plans must be developed in cooperation with the concerned external departments or organizations.

13.5. Easy-to-read boards defining general responsibilities for emergencies must be installed at different locations throughout the building.

13.6. To reduce the damages caused by the incidents in the building, the emergency response plan must cover the following aspects:

13.6.1.	    Scope;

13.6.2.	    Objective;

13.6.3.	    Definitions;

13.6.4.	Planning scenarios based on previous risk evaluations;

13.6.5.	Emergency levels;

13.6.6.	The members of the crisis management team, their roles and responsibilities (crisis management team and the on-scene emergency response team);

13.6.7.	A diagram, schematically illustrating the emergency response plan and determining the internal and external relations, contractors, emergency levels, communications between the members of the crisis management team and the on-scene emergency response team;

13.6.8.	The ID cards of the members of the Emergency Management Team (EMT) and Crisis Management Team (CMT);

13.6.9.        The equipment and facilities in the crisis management room;

13.6.10.	Emergency response drills;

13.6.11.	Emergency response drill operating manual;

- Contractors

- NIOC headquarters;

- Emergency telephone numbers, the addresses and the list of equipment and facilities available in the building and those of external organizations (hospitals, airports, the fire department, etc.);

- Checklists for developing emergency scenarios and evaluating drills;

- Methods of egress, evacuation, and the assembly area;

- Methods of communicating with the media;

- The fire department and HSE organizational charts;

- MEDEVAC methods (from the in the building to the hospital).

# 14	Miscellaneous

## 14.1	Using Flammable Fluids

Using flammable and toxic fluids to clean the floor is prohibited in all buildings.

## 14.2	Smoking

According to the directive 80879-92/1 of the minister of petroleum, dated 5/18/2013 (Appendix 1), smoking tobacco is prohibited inside all buildings and it is necessary to designate a smoking area where the individuals are allowed to smoke.

## 14.3	Building Electrical Safety

Electricity is a major cause of disabling injuries, loss of lives, and fire in buildings. Therefore, it is essential that, in addition to the following measures, the requirements of Chapter 6 of the NIOC General Safety Regulations and Chapter 13 of the National Construction Regulations (Electrical Installations) are also complied with.

	Necessary arrangements in the design of buildings shall be planned and made to prevent electrical hazards.

	The cables and cords of electrical devices such as computers, calculators, desk lamps, etc. must be covered and organized appropriately to protect the individuals from getting caught in them and falling.

	The use of electrical devices such as space heaters, desk lamps, tea makers, etc. that are not approved and installed by the maintenance and technical services unit of the building and the fire department is prohibited. In addition, it is necessary that these devices are approved by the safety and fire department upon purchase.

- Connecting multiple electrical devices to the same receptacle is prohibited.

- Electrical devices and equipment shall not be repaired by unauthorized individuals.

- The use of daisy-chained cables and cords is prohibited.

- To prevent the accumulation of loose cords, sufficient receptacles must be installed at appropriate locations that can be used easily.

- Receptacles must be grounded and located at safe and appropriate spots where they do not pose as electrocution hazards.

- The receptacle shall not be installed on the floor.

- The lightning arrester and grounding systems must be inspected, tested, and accepted according to the standards of the concerned units.

- The diesel fuel for the emergency generator must be inspected and tested periodically.

- The electrical enclosures inside office buildings must be inspected according to the preventive maintenance plan.

- In cases where a radio tower is implemented in the office building, it is essential that the tower has a separate grounding system.

- The electrical enclosures must be equipped with separate miniature fuses for different components such as the bathrooms, kitchen, rooms, the air conditioning system, the boiler room, etc.

- The electrical enclosure must be located near the main entrance and inside the building.

- Every electrical enclosure must be equipped with a circuit breaker.

- The electrical cables and tubes must run through separate ducts or inside the walls.

- It is essential that the elevator, the fire escape, dark cellars, and the boiler room are powered by a 12 V emergency supply integrating batteries and automatic charging relays.

14.4 Requirements for Construction near Filling Stations and Fuel Reserves

14.4.1. The fuel tanks of the fuel (petrol and gas) stations must be located at least 7 meters away from the adjacent buildings and public ways.

14.4.2. Construction of cinemas, assembly halls, schools, mosques, or other public buildings is not allowed adjacent to fuel stations.

# 15	General Notes on Fire Prevention in Buildings

15.1. In all buildings, to prevent fire and its spread, the doors and windows must be opened and closed easily so that the spread of fire and heat through half-open doors can be prevented.

15.2. Lack of space and densely-packed combustibles in buildings can contribute to the rapid spread of fire. In multi-story buildings, heavy machinery and equipment must be placed in the lower floors to prevent their collapse in the event of a fire when the structure is weakened.

15.3. Combustible fluids and gases must be stored outside the buildings and brought in only as much as needed.

# 16	References

1. NIOC General Safety Regulations. 2. National Construction Regulations, Chapter 3, Building Fire Protection, 2013.

3. National Construction Regulations, Chapter 21, Civil Defense, 2012.

4. National Construction Regulations, Chapter 22, Care and Maintenance, 2013.

5. National Construction Regulations, Chapter 13, Electrical Installations, 2003.

6. Tehran Firefighting and Urban Safety Services Organization and National Regulations.

7. BS‐EN 54 and NFPA 72 standards.

# 17	Appendices

## Appendix 1. Directive on the Prohibition of Smoking

From: 	Minister of Petroleum

To: 	Esteemed deputy ministers

Esteemed deputy ministers and chief executives at parent companies

Managers of staff units

Subject: Smoking prohibition

In regard to the Comprehensive National Tobacco Control Law (2006) and to prevent the use of tobacco products for their damaging impact on national production and to protect the workforce, as the most valuable assets and national wealth, the following are notified for implementation and supervision:

- Smoking any type of tobacco products by any means is prohibited in the office areas - whether indoor or outdoor - facilities, buildings, and operating and service fields. The authorities are required to install “No Smoking” signs in adequate numbers in places that can be seen easily.

- Smoking in the rest and recreational areas and facilities used by the workers in the oil industry or their families is also prohibited, which must be enforced and notified repeatedly.

- To prevent and control the use of tobacco, a “supervisory council” is formed composed of representatives from Deputy for Human Resource Development  and Management (Head), the Health Organization (Secretary), Public Relations, HSE and HRD departments of the four parent companies, and the Security Department with the aim of policy-making, supervising the implementation of the plans, following up the legal requirements, developing executive procedures, and preparing periodic reports on the progress.

- The prohibition of smoking must be mentioned in the public recruitment announcements and smokers shall no longer be employed and the employment of those contracted employees who are known to smoke cannot be turned into permanent.

- The security department will be responsible to control and introduce the violators to the authorities to be investigated by the disciplinary committee.

- In addition to setting a deadline for the employees to quit their habits, the authorities are required to support their employees by providing medical and consultation services to help them successfully quit smoking.

- The Petroleum Industry Health Organization (PIHO) is responsible for offering preventive, educational, medical, and rehabilitation services for smoker employees, providing them with consultation and conducting practical research in this regard, while supporting consultation and rehabilitation centers in the twenty zones.

- in cooperation with the related experts, the public relations departments in the parent and subsidiary companies are required to plan scheduled, regular, and persistent promotions to educate the employees and their families about the downsides of smoking to reduce tendency to smoking and establish the health, social, and financial losses associated with smoking.

Rostam Qasemi

Appendix 2. Building Safety Checklist

| Building Safety Certificate |  |
| --- | --- |
| Building Location Layout | Building Name Building Address |
| The average number of visitors per day: (Permanent ......... /Contracted ......... /Contractors’ .........) Employees: Number of Employees: |  |
| Building: Year of Construction Structure Type: Reinforced Concrete Girder Other (Specify) ......... Facade: Stone Brick Cement Other (Specify) ......... Number of Floors ......... Land Area ......... square meters Building Height ......... Meters Built-up Area ......... square meters |  |
| Emergencies Number of Exits ......... Has Fire Escape Yes No Means of egress at the ground floor (exit) Has coordination been made with the neighboring fire stations? Yes No Distance to the nearest fire station ......... meters |  |
| Special units in the building (fill out the corresponding checklists for each case) Kitchen Boiler Room Warehouse Library Parking Lot Technical Workshop Other (Specify) |  |
| Insurance Is the property covered by insurance? Yes No Type of insurance (coverage) Fire Earthquake Other (Specify) ....... Insurance Limit IRR |  |
| The person in charge of building maintenance: Telephone/Fax. Emergency Telephone Number. Auditor: Signature |  |

Appendix 3. Building Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Has a risk assessment been undertaken for the building? | General Safety | 1 |
|  |  |  |  | If applicable, is appropriate Personal Protective Equipment (PPE) used? |  | 2 |
|  |  |  |  | Have all chemical containers been labeled? |  | 3 |
|  |  |  |  | Is the chemical storage location suitable and are adequate safety measures in place for their storage and handling? (For example, are the containers that are placed at a height secured properly?) |  | 4 |
|  |  |  |  | Is there a list of chemicals and their SDS available? |  | 5 |
|  |  |  |  | Have the employees been trained about and acquainted with the SDS of the chemicals? |  | 6 |
|  |  |  |  | Is there a first-aid cabinet, including the essentials, in the location? |  | 7 |
|  |  |  |  | Is the location ventilated properly to prevent temperature rise and chemical contamination? |  | 8 |
|  |  |  |  | Is there a workshop management system in place that requires the workplace to be cleaned and organized regularly? |  | 9 |
|  |  |  |  | Are the entrances/exits (floor, hallway, etc.) obstructed by any object? |  | 10 |
|  |  |  |  | Is the floor kept dry and non-slippery at all times? |  | 11 |
|  |  |  |  | Have railings been installed in the staircases? |  | 12 |
|  |  |  |  | Is the staircase free of defects, such as worn-out or broken edges? |  | 13 |
|  |  |  |  | Have electrical hazard signs, labels, and warnings been installed in appropriate places? |  | 14 |
|  |  |  |  | Have signs, labels, obstructions, and warnings about emergency egress been installed and the means of egress specified? |  | 15 |
|  |  |  |  | Have signs, labels, and warnings for entering restricted areas been installed? |  | 16 |
|  |  |  |  | Are the heavy equipment and goods located at lower floors? |  | 17 |

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Are there unsafe shelves with sharp edges? | General Safety | 18 |
|  |  |  |  | Are the bookshelves, files, etc. secured to the wall properly? |  | 19 |
|  |  |  |  | Are emergency exit maps installed on the walls in the hallway, in the elevators, and at the building entrance? |  | 20 |
| (These doors must open to the hallways) |  |  |  | Does the building have emergency exits? Are they accessible and opened easily? |  | 21 |
|  |  |  |  | Are muster points specified and announced? |  | 22 |
|  |  |  |  | Are the emergency exits shut tightly or equipped with a self-shutting mechanism? |  | 23 |
|  |  |  |  | Does the building have a functional fire-escape? |  | 24 |
|  |  |  |  | Are the means of egress equipped with emergency illumination? |  | 25 |
| (Obstructions (chairs, etc.) left in the doorways, hallways, and stairs) |  |  |  | Are the means of egress manger properly? |  | 26 |
| (General rule: an assembly hall must have more than one exit) |  |  |  | Is the conference hall sized appropriately in the number of seats, exits, etc.? |  | 27 |
| Last edition (date): |  |  |  | Has an ERP been developed? |  | 28 |
| According to the building risk assessment |  |  |  | Have the employees received emergency response training and are they aware of their responsibilities and how to meet them according to the ERP? |  | 29 |
| Medical emergency, fire department, etc. |  |  |  | Are emergency telephone numbers listed visibly and installed at an appropriate place? |  | 30 |
| Last undertaken drill (date): |  |  |  | Was the drill undertaken according to risk assessments? |  | 31 |
|  |  |  |  | Do the rooms have people or seats in excess of their capacities? |  | 32 |
|  |  |  |  | Are the fall-protection railings installed on the roof suitable? |  | 33 |
|  |  |  |  | Is access to the roof restricted? Are the access routes safe? |  | 34 |
|  |  |  |  | Has a manual or work permit system (cold and hot) been developed for activities in the building? |  | 35 |

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
| The number of elevators: The allowable payload capacity in each elevator: |  |  |  | Is a visible sign installed in the elevator showing its loading capacity? |  | 36 |
|  |  |  |  | Are the elevators regularly inspected? |  | 37 |
|  |  |  |  | Is a valid certificate of integrity issued and installed in the elevator? |  | 38 |
|  |  |  |  | Is a valid insurance installed in the elevator? |  | 39 |
|  |  |  |  | Do elevators stop exactly at floor level? |  | 40 |
|  |  |  |  | Do the elevator door sensors function properly? |  | 41 |
|  |  |  |  | Are there communication devices inside the elevator? |  | 42 |
|  |  |  |  | Is there an emergency telephone number to be found in the elevator? |  | 43 |
|  |  |  |  | Does the elevator cease to function during a fire? |  | 44 |
|  |  |  |  | Does the elevator ventilation system function properly? |  | 45 |
|  |  |  |  | Is there a visible “Do Not Use the Elevator in the Event of a Fire” sign installed in the elevator? |  | 46 |
|  |  |  |  | Is the server room equipped with proper safety measures (ventilation, grounding, etc.)? |  | 47 |
|  |  |  |  | Are "Smoking Prohibited" signs installed on every floor? | Fire Safety | 48 |
|  |  |  |  | Is a safety and firefighting equipment layout plan available in the building? |  | 49 |
|  |  |  |  | Is the building equipped with an addressable fire alarm system? |  | 50 |
|  |  |  |  | Can the sound of the fire alarm be heard clearly everywhere inside the building? |  | 51 |
|  |  |  |  | Is the building equipped with firefighting devices and automatic fire suppression system? |  | 52 |
|  |  |  |  | Are there enough fire extinguishers (manual and automatic) that are suitable for the fire hazards in the building? |  | 53 |

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
| Specify the number of fire extinguishers on each floor. |  |  |  | Are the fire extinguishers installed at accessible locations according to the standards? |  | 54 |
| The date of the last inspection must be specified. |  |  |  | Are the extinguishers regularly and periodically inspected? |  | 55 |
|  |  |  |  | Is it clear who is responsible for the inspection and maintenance of the manual/automatic alarm and suppression equipment? |  | 56 |
| Review the documents |  |  |  | Are the fire alarm and suppression equipment inspected and maintained regularly and periodically? |  | 57 |
|  |  |  |  | Is there a firefighting water supply and distribution system? |  | 58 |
|  |  |  |  | Is the firefighting water supply pressurization system functional? |  | 59 |
| The type of the fire pumps: |  |  |  | Are the firefighting water tanks in proportion to the requirements? |  | 60 |
|  |  |  |  | Has a fire truck been dedicated to the building, and is it possible to locate it near the building? |  | 61 |
|  |  |  |  | Are there enough breathing apparatuses? |  | 62 |
|  |  |  |  | Will the firefighting water pressurization system remain functional in case of power outage? |  | 63 |
| The related standards |  |  |  | Are the amount of the firefighting water and output pressure in proportion to the requirements of the building? |  | 64 |
|  |  |  |  | Are there fireboxes on all floors, and are they complete and functional? |  | 65 |
| Stored over palettes and out of direct sunlight |  |  |  | Are combustible materials and liquids such as paper, petroleum, and paint, stored safely? |  | 66 |
|  |  |  |  | Are organizational smoking prohibition directives implemented? |  | 67 |
|  |  |  |  | Are the chimneys, ventilation ducts, facility ducts, and smoke and air exhausts made of fire-resistant or refractory materials? |  | 68 |
|  |  |  |  | Are the personnel trained for using fire suppression equipment (extinguishers, etc.) periodically? |  | 69 |
| Specify the heating system. |  |  |  | Are gas burners used in the building? |  | 70 |
|  |  |  |  | Given the prohibition of using portable space heaters, are such devices used in the building? |  | 71 |
|  |  |  |  | Does the facade incorporate combustible materials (such as MDF, etc.)? |  | 72 |

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Are the engineering documents related to the design of the firefighting water pumping system (pumps, tanks, etc.) and the standard water requirements for fire suppression in the building available? |  | 73 |
|  |  |  |  | Are fire alarms and extinguishers accessible and visible? |  | 74 |
|  |  |  |  | Are the classified, important documents retained in a safe, fire-protected area? |  | 75 |
| Review the documents |  |  |  | Is the wiring system for the facilities and electrical devices inspected periodically by an eligible person? | Electrical Safety | 76 |
|  |  |  |  | Does the building have emergency illumination? |  | 77 |
| Extension cords shall not be used permanently, and are they being used appropriately? |  |  |  |  |  | 78 |
|  |  |  |  | Are the cables and wires covered and placed properly? |  | 79 |
| Cables shall not be placed beneath carpets or laid around the doorway |  |  |  | Do the cables run through special ducts and tangle-free? |  | 80 |
|  |  |  |  | Are electrical equipment protected by shielding and insulation? |  | 81 |
|  |  |  |  | Does the building have an electrical grounding system? |  | 82 |
|  |  |  |  | Are the electrical enclosures grounded properly? |  | 83 |
|  |  |  |  | Is there a manual for operating the electrical equipment? |  | 84 |
|  |  |  |  | Are the doors to the electrical room closed and monitored? |  | 85 |
|  |  |  |  | Is the building equipped with emergency illumination/power supply? |  | 86 |
|  |  |  |  | Is the electrical earthing or grounding pit in good condition? |  | 87 |
|  |  |  |  | Have lightning arresters been installed on towers, tall buildings, minarets, and the tall parts of the building? |  | 88 |
| Desks, chairs, etc. shall not be stored in the electrical room. |  |  |  | Is the electrical room kept free of irrelevant objects? |  | 89 |

Appendix 4. Warehouse Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Does the power distribution conform to safety standards? | Safety and Firefighting | 1 |
|  |  |  |  | Are the electrical enclosures located at safe spots? |  | 2 |
|  |  |  |  | Is there a fire alarm system in the warehouse? |  | 3 |
|  |  |  |  | Are suitable fire detectors installed? |  | 4 |
|  |  |  |  | Is there a fire suppression system in the warehouse? |  | 5 |
|  |  |  |  | Have suitable fire extinguishers been selected and maintained functional? |  | 6 |
|  |  |  |  | Are “Smoking Prohibited” signs installed in the warehouse? |  | 7 |
|  |  |  |  | Is the warehouse constructed of earthquake-and-fire-resistant materials? |  | 8 |
|  |  |  |  | Is the ventilation system in proportion to the size of the warehouse? |  | 9 |
|  |  |  |  | Is the temperature and humidity of the warehouse monitored? |  | 10 |
|  |  |  |  | Is the emergency illumination functional? |  | 11 |
|  |  |  |  | Are all objects (shelves, files, etc.) secured properly against falling? |  | 12 |
|  |  |  |  | Are the workers equipped with suitable and sufficient PPE items (workwear, boots, aprons, etc.)? |  | 13 |
|  |  |  |  | Does the first aid kit contain all the necessities and is it installed at an accessible location? |  | 14 |
| Being informed of the SDS, not placing chemical containers at height, applying the safety labels, etc. |  |  |  | Are the chemicals handled and stored according to chemical management requirements? |  | 15 |
|  |  |  |  | Is the warehouse properly illuminated and ventilated? |  | 16 |
|  |  |  |  | Are the employees informed about and comply with the principles of safety and ergonomics in carrying loads? |  | 17 |

Appendix 5. Parking Lot Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Is there an air conditioning system in place? | Safety and Firefighting | 1 |
|  |  |  |  | Has the floor become slippery due to spilled oil products? |  | 2 |
|  |  |  |  | Does the parking lot have an emergency power supply? |  | 3 |
|  |  |  |  | In emergencies, is it possible to communicate with other units from the parking lot via telephone? |  | 4 |
|  |  |  |  | Is there electrocution or short-circuit hazards due to contact with water in the parking lot area? |  | 5 |
|  |  |  |  | Is there a risk of accidental collision with the electrical equipment? |  | 6 |
|  |  |  |  | Is there a fire alarm system in the parking lot? |  | 7 |
|  |  |  |  | Is there a fire suppression system in the parking lot? Are suitable fire detectors installed? |  | 8 |
|  |  |  |  | Have suitable fire extinguishers been selected and maintained functional? |  | 9 |
|  |  |  |  | Are the vehicles parked with standard spacing? |  | 10 |
|  |  |  |  | Is there a visible sign with the fire department telephone numbers installed in the parking lot? |  | 11 |
|  |  |  |  | Is the ventilation system in proportion to the size of the parking lot? Is fresh air supplied adequately? |  | 12 |
|  |  |  |  | Is there enough traffic hazard signs and labels (collision, fire hydrant location, etc.) installed? |  | 13 |
|  |  |  |  | Are the spots where parking is and is not allowed marked accordingly? |  | 14 |
|  |  |  |  | Are convex mirrors and traffic signs installed at locations where visibility is not enough? |  | 15 |
|  |  |  |  | Is the parking floor surface marked with lines? |  | 16 |
|  |  |  |  | Are you sure surplus objects and decommissioned vehicles are not kept in the parking lot? |  | 17 |

Appendix 6. Boiler Room Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Does the boiler room have an emergency power supply? | Safety and Firefighting | 1 |
|  |  |  |  | Are all devices and electrical equipment (pumps, etc.) in the boiler room grounded? |  | 2 |
|  |  |  |  | Are the manuals for all devices and pieces of equipment in the boiler room available? Are they installed somewhere? |  | 3 |
|  |  |  |  | Do all devices and pieces of equipment in the boiler room have a technical ID? |  | 4 |
| Inspection documents |  |  |  | Are the cables inspected to ensure their integrity? |  | 5 |
|  |  |  |  | Are there signs of improper wiring in the boiler room? |  | 6 |
|  |  |  |  | Is it possible to communicate with other units from the boiler room via telephone? |  | 7 |
|  |  |  |  | Is there electrocution or short-circuit hazards due to contact with water in the boiler room area? |  | 8 |
|  |  |  |  | Is there a risk of accidental collision with the electrical equipment? |  | 9 |
|  |  |  |  | Is there a fire alarm system in the boiler room? |  | 10 |
|  |  |  |  | Is there a fire suppression system in the boiler room? Are suitable fire detectors installed? |  | 11 |
|  |  |  |  | Is there a visible sign with the fire department telephone numbers installed in the boiler room? |  | 12 |
|  |  |  |  | Are “Smoking Prohibited” signs installed in the boiler room? |  | 13 |

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Is the ventilation system in proportion to the size of the boiler room? Is the fresh air supplied adequately? |  | 14 |
|  |  |  |  | Is a gas type detector installed in the boiler room? |  | 15 |
|  |  |  |  | Are water, steam, and fuel leaks recorded? |  | 16 |
| Technical inspection certificates (for the boiler, the grounding system, etc.) |  |  |  | Are the valid technical inspection certificates available? |  | 17 |
|  |  |  |  | Are the boilers maintained and logged regularly? |  | 18 |
|  |  |  |  | Are the pressure gauges inspected and calibrated regularly? |  | 19 |
|  |  |  |  | Are there enough flashlights in the maintenance department and the boiler room? |  | 20 |
|  |  |  |  | Is the boiler room floor free of bumps and holes? |  | 21 |
|  |  |  |  | Is the plan of the boiler room (including the fuel lines, cut-off valve locations, the electrical wiring, etc.) prepared and installed? |  | 22 |
|  |  |  |  | Are the ambient conditions acceptable in the boiler room (in terms of illumination, ventilation, noises, etc.)? |  | 23 |
|  |  |  |  | Is the workshop management acceptable? |  | 24 |
|  |  |  |  | Do the workers use proper PPE items and are they trained adequately? |  | 25 |
|  |  |  |  | Does the first aid kit contain all the necessities and is it installed at an accessible location? |  | 26 |

Appendix 7. Kitchen Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
| Documents |  |  |  | Has a risk assessment been undertaken? | Safety and Firefighting | 1 |
|  |  |  |  | Are the electrical wiring systems and receptacles in the kitchen and the dining halls in good condition? |  | 2 |
|  |  |  |  | Is there any sign of overheating in the electrical cables, or blown fuses, cut-offs, or the rupture of the insulation? |  | 3 |
|  |  |  |  | Are all electrical devices in the kitchen grounded? |  | 4 |
|  |  |  |  | Have signs, labels, obstructions, and warnings about emergency egress been installed and the means of egress specified? |  | 5 |
|  |  |  |  | Does the kitchen have an emergency exit and does it provide easy access to the outside? |  | 6 |
|  |  |  |  | Does the kitchen have an emergency power supply? |  | 7 |
|  |  |  |  | Is there a fire alarm system? |  | 8 |
|  |  |  |  | Are suitable fire detectors installed? |  | 9 |
|  |  |  |  | Is there a fire suppression system in the kitchen? |  | 10 |
|  |  |  |  | Have suitable fire extinguishers been selected and maintained functional? |  | 11 |
|  |  |  |  | Are the combustibles and garbage contained properly? |  | 12 |
|  |  |  |  | Is the ventilation system in proportion to the size of the kitchen? Is the fresh air supplied adequately? |  | 13 |
|  |  |  |  | Is the kitchen floor slippery? |  | 14 |
|  |  |  |  | Was the sewage system designed to prevent water accumulation over the surface? |  | 15 |
|  |  |  |  | Have proper hazard signs, labels, and warnings been installed in the kitchen, freezer, and the pantry? |  | 16 |
|  |  |  |  | Is the entrance to the walk-in freezer designed not to lock people in? |  | 17 |
|  |  |  |  | Are the workers equipped with suitable and sufficient PPE items (workwear, boots, aprons, etc.)? |  | 18 |
|  |  |  |  | Does the first aid kit contain all the necessities and is it installed at an accessible location? |  | 19 |
|  |  |  |  | Are health inspections carried out periodically? |  | 20 |

Appendix 8. Warehouse Fire Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Are the gas cylinders positioned vertically and secured tightly using a chain or belt? | Safety and Firefighting | 1 |
|  |  |  |  | Is there an emergency shower and eyewash station? |  | 2 |
|  |  |  |  | Is workshop management underway in the workplace? |  | 3 |
|  |  |  |  | Are devices equipped with proper safety shield and does it work? |  | 4 |
|  |  |  |  | Is there a functional fire alarm system? |  | 5 |
|  |  |  |  | Are fire extinguishers installed at appropriate locations? |  | 6 |
|  |  |  |  | Is an operating manual prepared and installed for every piece of machinery and equipment? |  | 7 |
|  |  |  |  | Are all objects (shelves, files, etc.) secured properly against falling? |  | 8 |
|  |  |  |  | Do the cranes and lift equipment have technical inspection certificates installed on them? |  | 9 |
| Records |  |  |  | Are the facilities, equipment, tooling, and machinery inspected carefully by eligible auditors at specific intervals? |  | 10 |
|  |  |  |  | Is a color coding system implemented? |  | 11 |
|  |  |  |  | Are the workers equipped with suitable and sufficient PPE items (workwear, boots, aprons, etc.) and are they using them while working? |  | 12 |
|  |  |  |  | Does the first aid kit contain all the necessities and has it been installed at an accessible location? |  | 13 |

Appendix 9. Library Safety Inspection Checklist

| Description/Inconsistencies | (NA) | No | Yes | Item | Subject | no. |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Are the electrical wiring systems and receptacles in the library in good condition? | Safety | 1 |
|  |  |  |  | Are all electrical devices in the library grounded? |  | 2 |
|  |  |  |  | Regarding the computers, are the cables and wires covered and placed properly? |  | 3 |
|  |  |  |  | Does the library have an emergency power supply? |  | 4 |
|  |  |  |  | Is there a fire alarm system? |  | 5 |
|  |  |  |  | Are suitable fire detectors installed? |  | 6 |
|  |  |  |  | Is there a fire suppression system in the library? |  | 7 |
|  |  |  |  | Have suitable fire extinguishers been selected and installed at a proper height? |  | 8 |
|  |  |  |  | Is the library floor free of uneven surfaces? |  | 9 |
|  |  |  |  | Have emergency exit signs, labels, and warnings been installed? |  | 10 |
|  |  |  |  | Does the library have an emergency exit and can it be accessed quickly? |  | 11 |
|  |  |  |  | Are all objects (shelves, files, etc.) secured properly against falling? |  | 12 |
|  |  |  |  | Is the illumination and ventilation condition acceptable in the library? |  | 13 |
|  |  |  |  | Are the employees informed about and comply with the principles of safety and ergonomics in carrying loads, working with computers, etc.? |  | 14 |
|  |  |  |  | Does the first aid kit contain all the necessities and is it installed at an accessible location? |  | 15 |
|  |  |  |  | Has the special archive been arranged for important documents and is it preserved in safety? |  | 16 |