National Iranian Oil Company Safety, Health and Environment Management Foam Supply Guideline Reviewing Translation; Confirmed by; Publication Date of English Version. Davood Naderi/ Laleh H. Abbasi Training & Performance Measurement Department; Mani Abdollahzadeh Rad/ HSE Manager; September 2018. Responsibility; Prepared by; Corroborated by; Approved by; Publication date. Full Name; Mani Abdollahzadeh/ Maryam Sadat Fatemi [Signed] Head of Safety and Firefighting Department Safety and Firefighting senior Specialist; Siavash Derafshi [Signed] HSE Director; Reza Khalili [Signed] Non-industrial operations Deputy; Ali Kardor [Signed] CEO; November 2016. Position. Document Code: NIOC-HSE-SF-GU-026-00 Revision date: November 29, 2016 Revision No.: 0

Table of Contents

1. Introduction	3

2. Objective	4

3. Scope of Application:	4

4. Definitions and Terms	4

5. Legal References and Requirements:	5

6. Roles and Responsibilities:	5

6-2 Procurement and Supply Department	5

6-4 Foam Assessment Committee	6

	Membership requirements:	6

7. Types of Foam:	7

	Protein foam:	7

	Fluoroprotein foam (FP):	7

	Film Forming Fluoroprotein Foam (FFFP):	7

	Aqueous Film Forming Foam (AFFF):	8

	Alcohol Resistance Aqueous Film Forming Foam (AR-AFFF):	8

	Alcohol Resistant Film Forming Fluoroprotein Foam (AR-FFFP):	8

	Synthetic Detergent Foam:	8

8. Foam Procurement Process	9

8-1 Foam Type Selection with Respect to the Flammable Substances Used in the Industry	9

8-2 Calculation of the Required amount of Foam	9

8-4 Manufacturer/Supplier Selection and Purchase Process	10

8-6 Storage Conditions and Methods	14

# 1. Introduction

As most fire incidents in the oil industry are caused by petroleum and its derivatives and since water cannot be used to suppress such fires due to its large volumetric mass, firefighting foams are the only substances used in dealing with such cases.

Firefighting foams have a smaller specific weight than most flammable liquids and cover petroleum substances like a light blanket.

The floating foam covers the liquid's surface, containing the fire caused by the vapors emanating from the liquid.

Foam bubbles are used to control and suppress fire by:

- Preventing air (oxygen) from reaching the fuel by covering its surface

- Separating the flame from the fuel’s surface

- Containing the flammable vapors

- Preventing thermal radiation, and in turn, reducing the heat flux from the flame to the fuel’s surface (preventing the formation of flammable vapors)

- Colling off the fuels’ surface and metallic surfaces as the foam solution is losing its initial form (forming thin vapors and reducing the oxygen level in the vicinity of the fuel)

The present document was prepared to help handle the firefighting foam procurement process and closely supervise the whole process of supplying standard high-quality foams. It is aimed at providing the necessary requirements for the implementation of the different phases constituting the foam supply process. These phases include communication of supply needs, calculation of the required amount of foam, foam type selection with respect to the flammable substances used in the industry, use, storage, and disposal.

# 2. Objective

This document was prepared to help organize and standardize the foam procurement process, improve the quality of purchased foam, supervise all the procurement phases, manage the amount of the purchased foam, and prevent the purchase of extra foam throughout NIOC and its affiliates.

# 3. Scope of Application:

The present document applies to all NIOC’s subsidiary and associate companies, and departments.

# 4. Definitions and Terms

- Company: Hereafter in this document, the word “Company” shall mean “National Iranian Oil Company (NIOC)”.

- Associate companies: Associate companies shall include all production, operational, engineering and service companies affiliated with NIOC.

- Subsidiaries: Subsidiaries shall include oil and gas production companies and operational areas affiliated with the associate companies.

- Field test authority: The field test authority is a qualified laboratory and/or the Iranian National Standards Organization’ partner laboratory chosen to perform field tests.

- Iranian National Standards Organization’ partner laboratory:  Iranian National Standards Organization’ partner laboratory is a qualified laboratory certified by the Iranian National Standards Organization to perform laboratory tests.

- Firefighting foam: Firefighting foam consists of a collection of air bubbles made of an aqueous solution at the right concentration.

- Foam concentrate: Foam concentrate is a liquid, which combined with water at the right concentration produces the foam solution.

- Foam solution: Foam solution is a solution consisting of foam and water.

# 5. Legal References and Requirements:

- International standards such as ISO 7203, BS EN 1568, NFPA 11

- Iranian National Standard No. 3778-1 (2013), fire extinguishing substances, foam concentrates

- Part 1: Low expansion foam concentrates, for use in liquids - Non-water soluble - Properties

- Standards of Ministry of Petroleum: IPS-M-SF-140 and IPS-M-SF-142

- NIOC Waste Management Guideline: NIOC‐HSE‐EN‐GU‐006‐00

- Ministry of Petroleum General Directorate's Firefighting Foam Procurement and Approval Instruction No. MOP-HSED-In-208(1)

# 6. Roles and Responsibilities:

6-1 CEOs

- Ensuring the supply and allocation of financial resources and provision of the facilites required for the procurement of standard high-quality foam for operational units

- Ensuring the fulfillment of the guideline’s requirements

## 6-2 Procurement and Supply Department

- Supervising the firefighting foam procurement process

- Identifying the reputable foam manufacturing companies

- Supplying standard high-quality foam as requested by the relevant unit

6-3 HSE Department

- Preparing a firefighting foam procurement procedure/instruction based on the present guideline and interacting with the relevant departments

- Supervising the fulfillment of the requirements referred to in the instruction by the relevant departments through periodic inspections

- Providing the relevant personnel with the required training

## 6-4 Foam Assessment Committee

The committee shall consist of at least four members from associate companies. From among these members, one is from the HSE Department of the associate company's headquarters, two are representatives of HSE departments of subsidiaries/operational areas, and one is from the Procurement and Supply Department.

Note 1: At least half of the members plus one other member should be present at the site where the field test is being conducted.

Note 2: One representative from NIOC’s HSE Department will attend the committee as the supervisor on a case-by-case basis (this representative is not required to attend all the committee’s meetings).

## Membership requirements:

- The committee member should be a personnel of Safety and Firefighting Department.

- The committee member should have completed basic, intermediate and advanced (theoretical and practical) courses on firefighting foams and earned the relevant valid course certificate.

It should be noted that the representative of the Procurement and Supply Department is not required to earn the aforementioned certificate.

Committee Duties:

- Investigating and supervising all the phases of the foam procurement process according to relevant instruction

- Being present at the Iranian National Standards Organization’s partner laboratory when the field tests are being conducted

# 7. Types of Foam:

Today, the most common foams used in the firefighting industry include:

1. Protein foam

2. Fluoroprotein foam (FP) 3. Film forming fluoroprotein foam (FFFP) 4. Aqueous film forming foam (AFFF)

5. Alcohol resistance aqueous film forming foam (AR-AFFF)

6. Synthetic detergent foam

## Protein foam:

Protein foam is a type of foam concentrate derived from hydrolyzed proteins.

These foams provide a homogeneous and stable coverage, slowly suppress the fire, and are cost-effective.

Normal protein foams can be used with seawater and/or regular water. This type of foam should be mixed with air and used as air foam.

## Fluoroprotein foam (FP):

Fluoroprotein foams are protein foam concentrates with added fluorosurfactants.

These foams have a rather high thermal resistance. Beside preventing the recurrence of fire, they are used to suppress fires originating from hydrocarbon fuels and oxygenated additives.

Fluoroprotein foams can be used with seawater or regular water.

These foams should be fully mixed with air. They should never be used in nozzles without ventilation.

## Film Forming Fluoroprotein Foam (FFFP):

Film forming fluoroprotein foams have all the properties attributed to fluoroprotein foams. Additionally, they can form a thin aqueous film on the surface of some hydrocarbons, accelerating the fire suppression process.

Moreover, these foams are effective in preventing burn-back.

## Aqueous Film Forming Foam (AFFF):

Aqueous Film Forming Foam is a foam concentrate derived from a mixture of fluorinated and hydrocarbon surfactants. They can from an thin aqueous film on the surface of some hydrocarbons.

This type of foam is a made of a mixture of chemicals and synthetic foaming agents.

The layer covering the surface reduced  the surface tension of the foam solution, fully covering the hydrocarbon surface.

## Alcohol Resistance Aqueous Film Forming Foam (AR-AFFF):

Alcohol resistance aqueous film forming foam is made up of a mixture of synthetic detergents, chemicals, and polymers. Polar solvent fuels such as alcohols can destroy foams which are not resistant to alcohol.

Alcohol resistance aqueous film forming foams act like aqueous Film Forming Foam when faced with hydrocarbons, forming an aqueous film on the hydrocarbon surface.

## Alcohol Resistant Film Forming Fluoroprotein Foam (AR-FFFP):

Alcohol resistant film forming fluoroprotein Foam is made up of a mixture of fluoroprotein foam and polymers. When faced with hydrocarbon fuels, it acts like the film forming fluoroprotein foam, forming an aqueous film on their surface.

When used on polar solvents (or water soluble fuels), the polymer forms a thick film on the fuel’s surface. The film separates the foam from the fuel, avoiding any contact between the foam and the fuel and preventing its destruction.

## Synthetic Detergent Foam:

Synthetic detergent foams can be used to suppress small-scale hydrocarbon fires.

These foams are made of synthetic foaming and stabilizing agents.

Synthetic foams with average expansion ratios are used to suppress hazardous toxic vapors.

Different foams are used to suppress fires based on the different chemicals the fuels involved in the fires are made up. Foams with high expansion ratios are used in foam total flooding systems.

# 8. Foam Procurement Process

## 8-1 Foam Type Selection with Respect to the Flammable Substances Used in the Industry

As different foams have different applications, the Safety and Firefighting Department along with the Production Department shall determine the type of foam to be used in different cases based on the current available standards, including NFPA 11, 3778-1, and IPS-E-SF-140, and according to the following criteria: the process type, the flammable substances present at the operation site, the area’s weather and climatic conditions, the fire suppression systems accessible by each company, and the company’s type of activities.

## 8-2 Calculation of the Required amount of Foam

In order to properly manage the purchased foam and avoid purchasing extra amounts of foam inevitably destined to be disposed, the Safety and Firefighting Department shall perform a risk assessment according to Standard NFPA 11 (Section 6.12.9) and determine the amount of the foam required by different operational units according to the identified potential emergency scenarios, process type, equipment, and type and quantity of the flammable substances available at the site. The following should also be taken into consideration while determining the amount of the foam required by different units.

- The required amount of foam for fixed foam systems

- The required amount of foam for semi-fixed foam systems (e.g., the dry riser in tanks)

- The required amount of foam for portable foam systems (e.g., fire engines)

- The required amount of foam for practical training

- The average annual foam consumption during the past five years

- Special conditions (helping suppress fire at adjacent units, and special emergency conditions such as destruction of the foam tank)

It is recommended that a safety factor of at least 2 be considered for the estimated amounts.

Note 1: Companies with affiliates (subsidiaries/operational areas) should take into consideration the foams’ production date, the consumption rate, and the available stock at all their affiliates’ warehouses while calculating the required amount of foam. All the planning and management processes shall be based on the available stock at the warehouses so that, when placing an order for the foam needed by an operational area or operating company, the available stock at the warehouses associated with other areas and companies is checked. Moreover, foams are transferred between companies according to their expiry date to avoid waste of resources.

Note 2: The companies should determine the necessary minimum stock according to the required amount of the foam calculated as above so that when the stock reaches the minimum, a purchase request is automatically generated and acted upon.

8-3 Communication of Supply Needs

In this phase, based on the available stock, the purchase request is completed (according to the ongoing procedure at the relevant company) and submitted to the Procurement and Supply Department.

## 8-4 Manufacturer/Supplier Selection and Purchase Process

The call for bids for the purchase of firefighting foams is a two-stage process. These stages are as follows:

1. All the manufacturers/suppliers approved by the Iranian National Standards Organization are invited.  All the subsidiaries/associate companies are obliged to search for and collect the records of manufacturers/suppliers of firefighting foams.

2. Manufacturers/suppliers of firefighting foams submit their sealed enveloped bids while taking into consideration the details of the call for bids, as well as the type and quality of the foam requested by the owner.

3. Representatives of the requesting unit, Procurement and Supply Department, Commerce Department, and other departments involved should receive the sample firefighting foam from manufacturers/suppliers. The sample’s properties should comply with the those of the requested foam. The sample size should be enough so that it can be used in both laboratory and field tests and act as a control sample.

4. The representative of HSE Department should code the samples so that foams supplied by different companies be identifiable.

5. The coded samples are sent to the Iranian National Standards Organizations’ partner lab where their quality is assessed and relevant laboratory tests are performed on them.

Note 1: The laboratory tests should be carries out according to Standards No. 3778-1 and Appendix 7-1 of Ministry of Petroleum General Directorate's Firefighting Foam Procurement and Approval Instruction No. MOP-HSED-In-208(1).

Note 2: As long as the Ministry of Petroleum has no internal reference laboratory, samples should be sent to the relevant external laboratories based on the amount of the foam to be purchased. For the purchases of up to 20,000 liters, the samples are sent to one of the Iranians National Standards Organization’s partner laboratories. For purchased exceeding 20,000 liters, the samples are submitted to two separate Iranians National Standards Organization’s partner laboratories. If the results of the tests conducted by the two laboratories are contradictory, the samples are submitted to a third laboratory.

6. The sample of foams meeting the minimum standard in the laboratory test will be sent to the qualified field test authority.

All the members of the foam assessment committee should be present while the field test is being conducted.

Note 1: As, currently, the Ministry of Petroleum has no internal field test authority, a\the field test should be conducted by the Iranian National Standards Organization’s Partner laboratory and supervised by the associate companies’ foam assessment committee (Paragraph 4-5).

Note 2: The field test should be conducted according to the terms and conditions stipulated in Standard No. 3778-1 and Appendices 7-2 and 7-3 of Ministry of Petroleum General Directorate's Firefighting Foam Procurement and Approval Instruction No. MOP-HSED-In-208(1).

7. The sealed pocketed bids of companies whose foam samples have successfully completed the laboratory and field tests will be referred to the Tenders Commission.

8. The Tenders Commission will open the approved sealed pockets and announced the winner.

9. After the winner is determined and before the purchased foams are delivered, a sample of each batch ready to be delivered should be taken and compared with the relevant scalants and the tested sample provided by the same winner company.

10. If the qualitative properties f the submitted foams do not comply with those of the initially tested sample, the purchase will be rejected and the winner company shall be obliged to compensate for all the damages inflicted on the buyer (according to the relevant legal regulations).

11. The winner company should guarantee that the foam quality will not change during the commitment period. In the event of any quality change over the commitment period, the winner bidder shall be liable for the damages and has no right for objection.

12. As indicated in the relevant standard, the firefighting foam’s lifetime is 3-5 years. Foam suppliers should guarantee their foams for a period of at least three years.

Note: All the costs of laboratory and field tests shall be on the winning bidder. The possibilities shall be taken in to consideration while determining the call for bids terms and conditions and preparing the relevant documents.

A

B

B

Rejected

A

Receipt and storage

Approved

Rejection of samples and receipt of damages from the winning company

Testing of the purchased foam to compare it with the initial standard sample

Settlement of purchase contract

Approved

Investigation, assessment and selection of the winning bidder

Enquiry for organizing the call for bids

Rejected

Removal from the list of companies considered for call for bids

Field test

Foam sample

Rejected

Approved

Laboratory testing of foam samples

A

Receipt of samples from companies as requested

Calculation of the required amount of foam and determining the minimum stock

Figure 1 - Firefighting Foam Procurement Process Flowchart

Determining the approved companies

Purchase request

Selection of the required type of foam

8-5 Instructions for Use

The use of firefighting foam depends on the type of the flammable substance as it determines how the foam shall be applied and sprayed on the tanks or equipment on fire, the spraying duration and discharge, etc.. All such decisions shall comply with the available relevant standards including NFPA.

Note: The purchase and consumption of foam should be planned while taking the foam’s expiry date into consideration. In addition, foams with earlier expiry dates should be used in training programs, operational maneuvers, and other similar cases.

## 8-6 Storage Conditions and Methods

The following general considerations should be followed with respect to the storage of firefighting foams. In specific cases, the instructions provided by the manufacturer should be followed.

- Due to its low surface tension, foam can easily penetrate the openings in protective coatings and metals and accelerate corrosion.

- The corrosion accelerates if foam enters the water tank.

- If the tank's opening is covered, the stress and tension will crack its surface, letting foam enter the tank.

- The sediments will detach from the tank’s floor, potentially reducing the foam’s effect.

- Drying out of the foam's surface in the storage tanks and the falling dried foams will gradually create sediments.

- The FIFO (First-In, First-Out) storage system should be used for storing firefighting foams. According to this storage system, the foams with the earliest expiry dates will first leave the warehouse. In other words, the foams entering the warehouse will be stored according to their expiry date. Later, these foams will leave the warehouse according to their expiry date as well

The following storage conditions should be met when storing firefighting foams:

- The foam should be stored at the temperature and under the conditions provided by the manufacturer.

- The foam should be stored in corrosion resistant containers. Plastic containers are usually resistant to corrosion.

- As direct sunlight can alter the foam’s properties, the containers used for storing firefighting foams should not be exposed to direct sunlight.

- The foam should be stored in appropriate tanks and containers kept in a roofed area.

- The foam’s contact with air will alter its properties.

- Make sure the foam (both synthetic and protein) does not contact your eyes and mouth.

- When foams are mixed together, their aqueous film is destroyed, creating particles and altering their properties.

- Decanting foam is prohibited as it may contribute to foam rotting.

- Avoid mixing foams provided by different manufacturers, and different foams available at the storage, vehicle’s tanks, and fire suppression systems.

- Avoid adding water to the foam solution before use.

- The samples of the foams stored in the warehouse will be annually tested to ensure of their quality.

- Avoid opening the foam containers for no apparent reason. These containers should not be left open.

- Non-usable foams should be identified and separated from standard foams (Special training foams should be used for training).

- The warehouses where foams are stored should be inspected periodically to ensure foams are stored in proper containers and under favorable conditions.

8-7 Disposal

Foam waste should be disposed of according to NIOC’s Waste Management Guideline (NIOC-HSE-EN-GU-006-00).

Health, Safety, and Environment (HSE) Department

No. 17, Yaghma Alley, Jomhouri-e Eslami St. (btwn Hafez St. & Valiasr Ave.), Tehran, Tehran, Iran

Phone: +98 21 66726016, Fax: +98 21 6609723, SMS System: +98 10007615

HSEE@NIOC.IR	HTTP://HSE.NIOC.IR