National Iranian Oil Company Safety, Health and Environment Management Permit To Work System Guideline Reviewing Translation; Confirmed by; Publication Date of English Version. Davood Naderi/ Laleh H. Abbasi Training & Performance Measurement Department; Mani Abdollahzadeh Rad/ HSE Manager; September 2018. Responsibility/Subject; Prepared by; Confirmed by; Approved by; Publication date; Descriptions. Name; Mani Abdollahzadeh/ Maryam sadat Fatemi/Fatemeh Salimi/Jalal shayan Head of Safety and Firefighting Department /Senior Specialist of Safety and Firefighting Department; Siavash Derafshi/ HSE Manager; Roknodin Javadi/ CEO; April 2016. Position. Document Code NIOC-HSE-SF-GU-010-01 Revision date: April 09, 2016, Revision No.: 1

Contents

1. Introduction .............................................................................................................................................. 5

2. Scope ........................................................................................................................................................ 5

3. Purpose ..................................................................................................................................................... 5

4. Definitions ................................................................................................................................................ 5

5. Legal requirements ................................................................................................................................. 10

6. Permit To Work System (P.T.W System) .............................................................................................. 10

6.1 Implementation requirements for the P.T.W System ............................................................... 10

6.2 Activities that require obtaining permits .............................................................................................. 11

6.3 Activities that do not require a P.T.W system ..................................................................................... 13

6.4 Responsibilities and enforcement ........................................................................................................ 13

6.5 Actions required in the P.T.W system ................................................................................................. 16

6.5.1 Training and competence .................................................................................................................. 16

6.5.2 Communication ................................................................................................................................. 18

6.5.3 Documentation .................................................................................................................................. 18

6.5.4 Information contained in the permit form ......................................................................................... 18

6.5.5 Monitoring the P.T.W. system .......................................................................................................... 19

6.6 Preparation process .............................................................................................................................. 20

6.6.1 Coordination ...................................................................................................................................... 20

6.6.2 Planning ............................................................................................................................................ 20

6.6.3 Hazard identification and assessment ............................................................................................... 20

6.6.3.1 Toolbox Talk Risk Identification card (TRIC) .............................................................................. 21

6.6.4 Types/categories of work …………………...................................................................................... 21

6.6.5 Cross reference .................................................................................................................................. 22

6.6.6 Life/validity of permits ..................................................................................................................... 22

6.6.7 Isolation ............................................................................................................................................. 22

6.6.8 Precautionary measures ..................................................................................................................... 23

6.6.9 Gas testing ......................................................................................................................................... 23

6.6.10 Signatures ........................................................................................................................................ 24

6.7 Processes .............................................................................................................................................. 24

6.7.1 Display of permits ............................................................................................................................. 25

6.7.2 Suspension ........................................................................................................................................ 25

6.7.3 Shift hand-overs ................................................................................................................................ 25

6.7.4 Action in an emergency .................................................................................................................... 25

6.7.5 Reviewing, monitoring and controlling the permit ........................................................................... 26

6.8 Completion of work ............................................................................................................................. 26

6.8.1 Return of permit …………………………….................................................................................... 26

6.8.2 Site inspection ................................................................................................................................... 26

6.8.3 Cancellation of overrides .................................................................................................................. 26

6.8.4 Return to service ............................................................................................................................... 26

6.8.5 Logs/records ...................................................................................................................................... 27

7. Appendices ............................................................................................................................................. 27

8. References .............................................................................................................................................. 27

Appendix 1: Inspection checklist ............................................................................................................... 29

Appendix 2: Checklist for the Review of P.T.W. Systems ........................................................................ 31

Appendix 3: Hot Work Permit Form ......................................................................................................... 34

Appendix 4: Cold Work Permit Form ........................................................................................................ 37

Appendix 5: Isolation/Override (electrical/mechanical/instrumentation) Certificate ................................ 40

Appendix 6: Extended Period Isolation ………….................................................................................... 42

Appendix 7: Joint Area Permit ................................................................................................................... 43

Appendix 8: Joint Diving Permit ............................................................................................................... 44

Appendix 9: De-isolation for Testing Certificate ...................................................................................... 45

Appendix 10: Certificate for Putting Safety and Emergency Systems out of Service …........................... 46

Appendix 11: Certificate for Repairing Safety and Emergency Systems .................................................. 47

Appendix 12: Radiography Certificate ...................................................................................................... 48

Appendix 13: Excavation and Trenching Certificate ……......................................................................... 49

Appendix 14: Scaffolding Certificate ........................................................................................................ 50

Appendix 15: Confined Space Entry Certificate ........................................................................................ 51

Appendix 16: TRIC Card ........................................................................................................................... 52

Appendix 17: Sample of Certificate of Permit Issuance ............................................................................ 53

1. Introduction

The petroleum industry involves dealing large quantities of toxic and flammable materials; therefore, the potential of major accidents is always present. To prevent such accidents, it is vital to establish safe systems.

Human factors, such as failure to properly implement procedures are often a root cause of various accidents. These failures are due to lack of training, instruction or understanding of the purpose or practical application of a Permit to Work (P.T.W) system. A P.T.W is an essential part of a system and determines how a job can be carried out safely. It does not simply permit people to conduct dangerous jobs. The permit is a document used to eliminate or control all associated hazards and risks with the workplace. Issuing a permit does not make a job safe in and of itself. This goal can be only achieved by workplace preparation and through full implementation of the provisions contained in the permit.

A P.T.W system ensures that properly trained and authorized people avoid foreseeable risks using suitable precautions.

A P.T.W system is a key part of the HSE management system that is consistent with the legal requirements of the N.I.O.C. and prevents damage to people, facilities and the environment.

The N.I.O.C.’s Permit to Work Guideline specifies minimum requirements for controlling hazards (through P.T.W system) and subsidiaries shall prepare and develop relevant instructions in accordance with the provisions contained in this Guideline.

2. Scope

This guideline is applicable to all units of the N.I.O.C., including the subsidiaries, associates, managements and operational areas.

3. Purpose

- Defining the minimum HSE requirements for all P.T.W systems

- Performing non-routine and hazardous tasks in a safe manner

- Ensuring that people are aware of all hazards associated with their job as well as required preventive measures

4. Definitions

• Project

It refers to a set of temporary activities conducted using specific resources to achieve unique and sustainable results (product/service). A project can be a part of a plan.

• Employer

An employer is a legal person who is legally responsible for offering plans and projects in the area of oil industry to the contractor. The employer assigns projects to the other party (contractor) in accordance with the mutual agreement or contract.

• Executor

Executor is a natural person who is determined by an employer to execute a plan/project in coordination with other managerial and executive bodies.

• Contractor

A legal qualified person authorized to provide contracting services.

• Employer’s representative

Employer’s representative is a legal or natural person appointed by the employer to monitor the proper execution of operations/provision of services and to supervise proper implementation of HSE requirements by the contractor, in accordance with the available contract. Therefore, this person shall fully convey employer’s opinions and ideas (without manipulation) to the contractor in the area of health, safety and environment.

• Contractor’s HSE representative

Contractor’s HSE representative is a person appointed by the contractor and introduced to the employer to monitor, implement and follow up HSE affairs within the scope of the contract. The employer’s HSE unit shall evaluate the contractor’s HSE representative and declare his/her competence.

• Work Permit

This form permits authorized persons to carry out the work specified by an employer, in a safe manner, at the specified time and in the specified place. This form also specifies other safety measures that must be taken by personnel and managers. Considering the definitions of hot work and cold work, permits are prepared in two forms, namely “hot work permit” and “cold work permit”.

• Cold work

This type of work does not involve the use of any flame or thermal/spark-ignition devices or severe pressure that may cause combustion of flammable gases.

• Hot work

This type of work involves generating heat that can ignite flammable gases or vapors or the use of welding machines or devices that produce sparks or heat.

• Additional certificate

In addition to the main permits (hot and cold permits), a number of works require additional permits or certificates on account of their great sensitivity and significance. This indicates that additional precautionary and safety measures should be taken when performing such tasks. Some of the most prevalent additional permits or certificates include:

- Isolation/Override (electrical/mechanical/instrumentation) Certificate

- Certificate for Repairing Safety and Emergency Systems

- Certificate for Putting Safety and Emergency Systems out of Service

- De-isolation for Testing Certificate

- Scaffolding Certificate

- Confined Space Certificate

- Excavation and Trenching Certificate

- Radiography Certificate

• Joint Area Permit

This type of permit is used when two units or different facilities intend to coordinate their activities in a joint area. The management of each unit should be informed of what the other unit is performing in the joint area and vice versa (e.g. performing drilling activities besides oil platforms).

• Joint Diving Permit

This permit is used to notify other adjacent units that diving operations are performed in a unit and to prepare needed isolation certificates to protect divers.

• Isolation certificate

This certificate is attached to the permit to control and isolate/de-isolate electrical, mechanical and safety systems.

• Certificate for Repairing Safety and Emergency Systems

This certificate is used to control the sequence of isolations or disconnect them in order to repair and maintain safety and emergency systems.

• Certificate for Putting Safety and Emergency Systems out of Service

This certificate is attached to the main permit to remove safety systems. Examples include: putting flammable gas detectors out of service for welding operations and restarting them after completion of work.

• Gas Testing Certificate

Measuring and recording the quantities of toxic and flammable gases and oxygen in the workplace, before and during work (e.g. when performing hot work or in confined space operations).

• De-isolation for Testing Certificate

This certificate is used to examine the success level of completed work (e.g. cancelling isolations to test a repaired pump to ensure suitable sealing).

• Details on Mechanical Isolation

In cases where there is not enough space on the isolation certificate form, this form is used to describe issues associated with isolation in details.

• Scaffolding Certificate

This certificate is used when installing, executing and dismantling scaffolds. Histories of scaffold inspections are also recorded in this form.

• Confined Space Certificate

This certificate is associated with confined space entry/exit, in accordance with the relevant requirements.

• Excavation and Trenching Certificate

This certificate is issued by qualified persons for carrying out industrial radiography.

• Radiography Certificate

This certificate is issued by qualified persons for excavation, ditching and trenching.

• Lower Explosive Limit (L.E.L)

It is the lowest concentration of gas or vapor in air that is capable of producing an explosive compound. Volume percent is used to express this criterion.

• Upper Explosive Limit (U.E.L)

It is the highest concentration of a gas or vapor in air that is capable of producing an explosive compound. Volume percent is used to express this criterion.

• Hazardous (forbidden) areas

Hazardous areas are defined as “areas, where there is a risk of fire, explosion, toxic substances release, etc. due to operational conditions and common processes”.

• Classification of hazardous areas

Work areas are classified in terms of the hazard of dangerous atmospheres. This helps relevant personnel choose suitable electrical equipment and put them properly in the workplace.

• Zone 0:

In these areas, dangerous atmosphere (considerable quantities of flammable gases in the air, between the upper and lower explosive limits) is present continuously or for long periods of time.

• Zone 1:

In these areas, dangerous atmosphere is likely to arise in normal operations and all precautionary and safety measures must be taken at any time.

• Zone 2:

These areas are safe in normal conditions; however, hazardous materials and gases may be released at any time for various reasons.

• Applicant/Originator

Applicant is a person who requests performing a task in a unit, on the basis of relevant permit. For example, Technical Inspection Unit may request performing specific repairs on process equipment in an operational unit.

• Permit issuer (Area Manager/Area Supervisor)

This person issues permits for various activities. He/she ensures full observance of safety precautions and that all needed signatures have been obtained.

• Person in charge of the work (supervisor)

This person supervises workers engaged in a task subject to a P.T.W system.

• Hand-over

It refers to the process of transferring responsibility for work activity between shift workers.

• Suspension

It refers to the temporary invalidation of a permit for a period during which the work has been stopped.

• Cancellation/Override

It refers to the temporary bypass of a safety device to allow certain work to proceed over a specified period (e.g. fire detector overridden during welding operation)

• Validity

It refers to the period during which a permit remains active and valid.

• Isolation

It refers to the process of putting a mechanical or electrical barrier between a source of energy and a place of work.

• Revalidation

In this process, working conditions are re-assessed to determine whether the work can be continued or not. The process requires the request of the person in charge of the work and agreement of the permit issuer.

• Monitoring

The routine checking of how the P.T.W system is being used on the job.

• Audit

Audit refers to the examination of the P.T.W system in order to assess the system over a specified time period.

• Review

In this process, the entire system is reexamined and required changes are identified to ensure the proper design and implementation of the P.T.W system.

• Verification

It refers to the whole process of examining the P.T.W system through daily monitoring to periodic audits and reviews to ensure that the system is continuing to function as intended.

5. Legal requirements

5.1 The special safety regulations of the N.I.O.C, adopted in 1974

5.2 The regulations of the Iranian Ministry of Labor and Social Affairs

5.3 All guidelines, instructions and procedures provided by the N.I.O.C.

6. Permit To Work System (P.T.W System)

6.1 Requirements for the implementation of the P.T.W System

The following requirements are necessary to ensure the proper implementation of the P.T.W system:

6.2 Activities that require obtaining permits

The P.T.W system is used to supervise activities with a hazardous nature (all hot work activities, high-risk cold work activities carried out in hazardous environments, repair activities, etc.) or those performed in hazardous environments. The following flowchart can be used to determine whether an activity requires a permit.

Examples of activities requiring a P.T.W system:

• Any type of activity involving the generation of heat. Examples include: welding, flame cutting, grinding, sandblasting, etc.

• Activities which may generate sparks

• Activities which may cause an unintended or uncontrolled hydrocarbon release, including working on any pipeline, vessel or equipment containing flammable or toxic materials

• Activities that involve the use of dangerous substances, including radioactive materials and explosives

• Working at height and where there is a risk of falling objects

• Risky load transfer operations

• Etc.

6.3 Activities that do not require a P.T.W system:

“No Permit Job” forms must be completed for all activities that do not require a P.T.W system. This form is completed for activities that do not include:

- Works carried out in operational/process areas

- Works carried out in environments with hydrocarbons, gases and toxic liquids

- Works carried out on electrical installations

- Works carried out in confined spaces

- Works requiring additional certificates

6.4 Responsibilities and enforcement

Individuals/organizations have specific duties and responsibilities specified in the P.T.W. system. The following authorities are responsible in this process:

1. Manager/Managing Director

2. Facility manager

3. Permit issuer

4. Supervisors or authorities

5. Staff (technician, welder, etc.)

6. HSE Department

7. Contractor’s representative

8. Project Manager/plan executor

These responsibilities include:

Note: According to this guideline, the subsidiary companies shall clearly specify the types of their activities, organizational structure, organizational posts and the job descriptions of those with key responsibilities in the P.T.W system and the positions of such personnel should be written in the permit form. In addition, an instruction must be developed to outline the process of selecting qualified person/persons.

1. The Managing Director shall ensure that:

- An appropriate P.T.W system is defined and established

- Training programs and competence standards are established and maintained

- Periodic monitoring/auditing/reviewing of the P.T.W. system is established and maintained.

2. The facility/shift/unit managers/supervisors:

They shall issue permits and monitor the proper implementation of the requirements of the P.T.W. system. They shall be fully acquainted with the nature of the work and all associated risks and shall ensure that:

- The permit is suitable for the desired work

- Effective inspections and tests are provided in the workplace

- All personnel who operate and use the P.T.W. system are competent

- The planning, issue and return of permits are properly coordinated

- The P.T.W. system information are effectively transmitted between personnel when passing their shifts

- The P.T.W system is regularly monitored to ensure its effective implementation

- All involved groups fully understand the nature of work and job descriptions

- All work-related hazards are identified and controlled

- All necessary precautions, including isolation, have been performed before commencing the work

- All necessary equipment have been labeled

- All people involved in the work, as well as those who may be affected by the work, are aware of the start, suspension and termination times

- The workplace is safe to continue the work

- Standby personnel are selected and other are determined to perform gas test

- People (both supervisors and executors) who are performing hazardous works simultaneously in one unit are fully aware of the presence of each other.

- Adequate time is given during shift changes to ensure effective transfer of information

- Reviewing and confirming the termination of the work and writing it in the issued permit

3. Supervisors (or people in charge of the work)

These people shall ensure that:

- They have received training in the P.T.W system as applied in that particular location

- Safe working procedures are available to all staff

- They discuss the job fully with the person issuing the permit

- The permit is posted at the work site

- The executor is aware of all potential hazards in the workplace

- The precautions are maintained throughout the work activity

- All workers understands that the work must be stopped and the situation must be re-evaluated upon any change in the circumstances

- The work group remains within the limitations set on the permit (physical boundaries, type of work and validity time)

- The site is left in a safe condition upon the completion or suspension of the work and the permit issuer is informed.

4. Individuals working within the P.T.W system (technicians, welders, etc.):

These individuals shall ensure that:

- They have received instruction and have a good understanding of the P.T.W. system as well as their workplace facilities

- They do not start work without obtaining a relevant permit

- They receive a briefing from the supervisor on the particular task and understand associated hazards and precautions

- They follow the instructions specified in the permit

- The site and all equipment are in a safe condition upon leaving the workplace

- They stop the work and consult with their supervisor upon encountering with abnormal circumstances

- They carry the permit with them when performing the work

5. Employer’s supervisor:

This person shall supervise and review requests submitted by executor/contractor for permits and shall monitor contractors in terms of conducting safe and proper work.

6. HSE Department

- Supervising the proper implementation of the P.T.W. system processes

- Ensuring safe work in high-risk activities

- Stopping the work in unsafe conditions

- Ensuring that the work does not interfere with other activities

- Ensuring that all documents have been reviewed and completed

- Before issuing new permits (confined space, isolation, etc.), the HSE department shall ensure the safety of workplace and review compliance with all relevant requirements.

- The HSE department certificates permit issuers and signers. Individuals shall undergo relevant training courses to obtain such certificates.

These certificates are valid for one year. An example of these certificates is presented in Appendix 17.

* To monitor the proper implementation of the P.T.W. system, the HSE department shall define and establish a suitable process.

7. The contractor’s representative

The contractor’s representative shall ensure that:

- Their employees are informed of the broad principles of the P.T.W system in the workplace

- Their employees have been given appropriate trainings (e.g. workplace hazards, necessary precautions, SDS, etc.) and understand the operation of the P.T.W system and their specific responsibilities within it

- They monitor and evaluate their employee competency, knowledge and skills continuously

Note: Once the contractor/contractor’s representative/contractor’s site manager signs a permit, he/she shall accept all legal consequences and the relevant contracting company shall be responsible for compensation of any damage to the N.I.O.C., third parties and the environment.

8. Project Manager/plan executor

All the requirements of this document should be established and implemented across the National Iranian Oil Company.

6.5 Actions required in the P.T.W system

6.5.1 Training and competence

To establish and implement a P.T.W system effectively, it is essential to have all key personnel within the system adequately trained. They shall undergo necessary training courses and obtain relevant certificates from the HSE Department.

The following training requirements are recommended for individuals performing various jobs:

1. The facility/shift/unit managers/supervisors:

Items that must be considered in the training include:

1. P.T.W system guidelines

2. Company policy, local rules and procedures

3. Responsibilities and communications

4. Procedures to identify work-related hazards and to control and remove them

5. Case histories of accidents or near misses involving failure of the P.T.W. system

In assessing for competence, consideration should be given to:

- The results of the training assessment

- Relevant work experience

- Full physical and mental health *

- Decisiveness

* It should be noted that in order to perform activities such as working at height and working in confined space, etc., the permit issuer shall ensure the appropriateness of the physical and mental conditions of the individual with the type of work.

The permit issuers should be able to demonstrate knowledge and competence in the following areas:

- Equipment layout

- Common process taking place, such as production, drilling, etc.

- Potential hazards

- The means of mitigating hazards before issuing a permit

- Specific responsibilities associated with issuing permits

- Applicable legal requirements

- Necessary precautionary measures before commencing the work

- All the company and local rules applying to the operation of the P.T.W. system

- Specific responsibilities of supervisors

- Shift handover requirements

- Action to be taken in an emergency situation

- Communication skills (for multi-language locations)

- Training requirements of different personnel

- Auditing and monitoring requirements

2. Persons in charge of the work:

shall be able to demonstrate knowledge and competence in the following areas:

- Potential hazards associated with the work

- Precautions required before commencing the work

- Local rules applying to the P.T.W. system

- Safety requirements contained in the permit

- Specific responsibilities of supervisors

- Shift handover requirements

- Action to be taken in an emergency situation

- Communication skills (for multi-language locations)

- P.T.W. training requirements for the job and for members of the work party

- Appropriate interaction and communication between permit issuer and persons in charge of the work

3. Company’s/Contractor’s supervisor:

shall be able to demonstrate knowledge and competence in the following areas:

- Potential hazards associated with the work

- Precautions required before commencing the work

- Local rules applying to the P.T.W. system

- Safety requirements contained in the permit

- Shift handover requirements

- Action to be taken in an emergency situation

- Appropriate interaction and communication between permit issuer and persons in charge of the work

4. Other members:

All other members of the workforce who are required to work within the P.T.W. system should receive instructions on the specific procedures as they apply on the installation where they are to work.

6.5.2 Communication

Due to the number of people who may be involved in the P.T.W. system and the potentially large number of interfaces, communication is one of the most important areas of a P.T.W. system. Special attention should be paid to the possibility of communication problems on sites.

Areas of specific emphasis include:

- Person requesting the work shall clearly state the exact nature and scope of the work, the number of workers, different trades and special tools involved.

- Person issuing the permit shall clearly communicate the potential hazards and precautions taken at the worksite. He should also ensure that any other person who may be affected by the work is informed.

- Person in charge of the work shall communicate to the members of his work party the information received on hazards and precautions and the action required in the event of an emergency.

- In the event of any change in work conditions, which may affect the validity of the permit, he should inform the permit issuer.

6.5.3 Documentation

Due to the importance of documentation in the P.T.W. system, documents shall:

- Be controlled

- Have a specific owner

- Be accessible

- Be periodically reviewed and amended if required

6.5.4 Information contained in the permit form

The “permit form” is one of the essential components of the P.T.W. system. Forms used in various companies may vary in structure and content, depending on the nature and type of activities; however, all forms shall be designed in a way to cover all activities and potential hazards. The two most common categories of forms are for hot work and cold work. However, additional permits or approvals are often issued for high-risk works, where more precautions and safety measures are required.

To facilitate the work, the administration of the permit system and control of work may be enhanced by using color combinations to distinguish between various permits; meanwhile, designers shall try to design simple and user friendly forms. It is also essential to write serial numbers and to print three copies of each form and complete them using carbon paper.

The following information shall be contained in the permit form:

- Permit number

- Serial number

- Description of tasks

- Description of exact location of site/area

- Details of work, used tools and restrictions

- Details of potential hazards

- Details of precautions taken

- Details of PPEs

- Notifying other relevant persons

- Time of issue and period of validity

- Signature of the person in charge of work

- Signature of the applicant

- Signature for handover of responsibilities between shifts

- Declaration by person in charge of work that work is complete or incomplete and site has been left in a safe condition

- Signature of person issuing the permit which confirms that site has been checked and that equipment may be reinstated or left safely isolated and that the permit is cancelled

A sample form is presented in Appendix 3.

6.5.5 Monitoring the P.T.W. system

A monitoring process shall be defined and enforced to ensure the proper establishment and implementation of the P.T.W. system. Examples include: assessment of the competence of the persons in charge of issuing permits, reviewing work processes in order to update new activities which require obtaining permits, etc.

The head of the operational unit, the head of the HSE Department and executors shall perform monitoring activities using available checklists within specific schedules.

These checklists can include the following questions:

- Is the permit properly displayed at the work site?

- Has it been properly completed?

- Is specified safety equipment in place?

- Are specified precautions adequate and being implemented?

- Do the personnel understand the permit terms and the nature of the work?

The checklists shall cover all aspects of the P.T.W system including isolations, adequacy of briefings, shift handover arrangements and training. This inspection should be carried out by senior personnel independent of the area being checked. It should be noted that the P.T.W system is usually a part of the safety audit process. The periodic review of the P.T.W system shall contain the results of previous audits, incident reports and legislation and organization changes.

See Appendices 1 and 2 for sample of audit checklist. To ensure compliance with the provisions contained in this guideline, the subsidiaries of the N.I.O.C. shall prepare and complete these checklists.

6.6 Preparation process

6.6.1 Coordination

To avoid the interference of simultaneous activities, requiring permits to work, coordination and planning shall be performed only by one person who is usually the head of the operational unit. This person will supervise the issuance and return of all permits.

In some facilities, this responsibility may be delegated to more than one person at various shifts. In these cases, the head of the operational units/facility manager often undertakes the main responsibility.

6.6.2 Planning

For activities requiring a permit, the following items should be planned before commencing the work:

- Identification of potential workplace hazards by supervisor

- Taking necessary precautionary measures and preparation for possible events

6.6.3 Hazard identification and assessment

A significant element of the P.T.W. preparation stage is an assessment of the hazards which may be associated with the work. Such assessment should be carried out by the permit issuer, in conjunction with the supervisor and any other persons whose specialist knowledge may be needed. The purpose is to eliminate, reduce and control the consequences of the identified and assessed hazards.

The following principles apply to assessments:

- Precise details of the work should be specified by the supervisor and safety considerations should be observed.

- The hazards associated with chemical substances (toxic, ignitable, etc.) and process equipment should be assessed.

- The practical difficulties of the work should be assessed and, if necessary, specialists in various units can provide consultancies.

- The interaction between the work and the surrounding environment should be assessed.

- To perform a safe job, necessary precautionary measures should be taken to eliminate, reduce and control identified hazards.

Examples of common hazards considered in hazard assessment process include:

- Pressurized liquid or gas

- Toxic materials

- Corrosive materials

- Flammable materials

- H2S area

- Direct flame or arc

- Flying  particles or sparks

- Radioactivity

- Moving Machinery

- Hot Materials

- O2 Deficiency

- Equipment Generating sparks

- Crane operation

- Pressure Testing

- Adjacent operations

- Wind, Weather, sea state

- Danger of Falling

- Access/egress

- Confined space

- Explosives

- Substances Harmful to Health

6.6.3.1 Toolbox Talk Risk Identification card (TRIC)

The permit issuer and the person in charge of the work shall hold meetings on TRIC. TRIC is a risk assessment process conducted at a specific location that focuses on identifying hazards at the site and time of work. TRIC shall be conducted before commencing the work.

A sample of TRIC form is presented in Appendix 16.

6.6.4 Types/categories of work

The types of work for which P.T.W. systems are normally applied include: maintenance and repair, inspection, testing, construction, dismantling, modification and cleaning.

The following works require obtaining a P.T.W system:

- Hot work of any type where heat is used and generated. Examples include: welding, flame cutting, grinding, sandblasting, etc.

- Works which may generate sparks or other sources of ignition

- Works which may cause an unintended or uncontrolled hydrocarbon release, including working on any pipeline, vessel or equipment containing flammable or toxic materials

- Electrical work

- Works at any place on an offshore installation from which any person could fall into the sea

- Works involving the use of dangerous substances, including toxic and radioactive materials and explosives

- Excavations

- Diving activities

- Pressure testing

- Danger of dropped objects

- Maintenance operations which compromise critical safety systems or which remove them from service. Examples include: fire and gas detection systems, public address systems, life-saving equipment and firefighting equipment.

The above list presents examples. Each company shall develop its own domestic list on the basis of its typical activities.

6.6.5 Cross reference

The objective of a cross reference is to ensure that no interaction takes place between work activities which might endanger the safety of personnel or facilities. The permit issuer shall be aware of the work environment, potential interaction when issuing different permits for the same piece of equipment or system or where there may be potential conflict with adjacent work activities and shall perform careful planning and take suitable precautions in these situations.

6.6.6 Life/validity of permits

There should be a limit on the life of a permit to ensure its applicability in various situations. Companies shall cancel permits at the end of each shift and in cases where the job continues beyond one shift, new permits shall be issued.

Each permit shall be cancelled at the end of each shift and a new one shall be issued by relevant authorities.

6.6.7 Isolation

Isolation is an essential element of a P.T.W system. Before conducting any maintenance or repair operation, the isolation principles shall be adopted in order to control potential hazards such as pressure, dangerous substances, lack of oxygen, moving machinery etc.

Each company shall develop its own isolation procedures to be adopted depending on work activity and risk involved.

The following points should be considered within the isolation procedures:

- Various isolations should be planned and recorded on a working drawing. This should be discussed between the person issuing the permit and the person in charge of the work to ensure all isolation points are clearly understood and agreed. The marked up drawings should be attached to a copy of the permit.

- The isolation standard shall be commensurate with the type of work, operating conditions and other effective factors

- The isolation procedures shall include all energy sources, such as mechanical, electrical, hydraulic pressure, etc.

- The tag or key number shall be recorded on the permit form or on a separate form which should in turn be cross referenced and attached to the P.T.W. form

- Isolation shall only be applied and removed by the person issuing the permit

- If more than one task is to be carried out on part of equipment, there is a risk that on completion of one of the tasks the isolations are removed and the equipment is put back into service. Controls should be in place to prevent early de-isolation

- If the work is not completed within the shift, the site should be checked by both the person in charge of the work and the permit issuer to ensure it is left in a safe condition and equipment cannot be reinstated until all work is properly completed

- If the permit is suspended, the status of the work site shall be left on display in a suitable location (e.g. the control room) and the isolation padlock keys shall be kept in a secure place to avoid unauthorized access

- All persons authorized to carry out isolations should be assessed for their competence prior to appointment. They should:

- Have adequate knowledge, expertise and skills

- Have relevant experience

- Have received specific instructions on the operational unit and isolation procedures

- Shall have passed relevant knowledge and skills assessment exams

Their areas of responsibility should be specified clearly.

6.6.8 Precautionary measures

The permit issuer and other relevant personnel shall specify necessary precautions on the permit or on another checklist. The supervisor of the work should ensure that all the precautions are put into operation.

The type of precautions will be specified based on the nature of the work. Some examples are provided below:

- The safety of personnel by using PPEs

- The safety of facilities or equipment associated with the work (e.g. isolation)

- The safety of all tasks (e.g. spark containment during welding)

6.6.9 Gas testing

In cases, where there is the possibility of existence of flammable or toxic gases or oxygen deficiency at the worksite, gas testing should be performed before issuing the relevant permit.

The following points shall be considered when performing the gas testing process:

- Persons involved in gas testing should be adequately trained in the use of gas testing equipment and in the interpretation of results. They should also hold valid certificates.

- The permit issuer shall specify the type of test, the sampling place and the type and number of samples. Gas testing should be done as close to the commencement of work as possible.

- Results of any gas testing should be recorded and timed and entered on the permit. In the case of any change during the work, the permit should be suspended.

- In some cases, the process and environmental conditions necessitate performing continuous gas testing and this issue should be specified in the permit.

- After performing the test, the work should be commenced within 2 hours. Otherwise, re-testing will be required.

- All gas and oxygen test devices should be calibrated by certified people.

- The exact testing time should be recorded in the permit form.

Note: Flammable gases (LEL and UEL measurement) should be tested by qualified personnel with valid certificates (operating personnel/permit issuers).

The representative of the HSE Department shall measure levels of toxic gases and oxygen and record them in the permit form.

6.6.10 Signatures

In the P.T.W. system, before commencing any work, certain signatures will be required. The number and designation of the signatories will be determined by the type of permit and the nature of the work.

As a minimum, the permit issuer and the person in charge of the work should sign the permit. Other personnel involved in the permit preparation (such as gas tester) should also sign the permit. The full name of individuals shall be written too.

Persons, who need to be aware of the permit or of aspects of the particular task, may also be required to sign.

Individuals can sign a permit after passing relevant training courses in the HSE Department and obtaining the required certificate (see a sample in Appendix 17).

The HSE Department should organize such training courses in accordance with the available timetable and in coordination with the Education Department. Where a transfer of responsibilities takes place, the new person should also sign the permit.

No one should authorize/issue a permit for work they will carry out themselves.

6.7 Processes

6.7.1 Display of permits

Permits should be displayed in the workplace, this way people who require them can access them readily whenever they need.

Copies of permits should be distributed and displayed as follows:

- At the worksite. Where this is not practicable, the person in charge of the job should always keep a copy with himself and ensure that all workers and personnel are familiar with its content

- At the control/coordination room. Here, it should be systematically recorded and archived.

- If the permit issuer is remote from the main control/coordination room, he should have a copy of the permit.

- The third copy of the permit shall be kept at the HSE Department.

The distribution process must be clearly specified in the P.T.W system executive procedures and guidelines.

6.7.2 Suspension

Works being carried out under a P.T.W. system may be stopped before they are completed.

Such circumstances include:

- In the event of an emergency

- Operational reasons to prevent interaction with other activities

- Work during a single shift

- Waiting for materials or services to arrive

In certain circumstances, the main permit may be cancelled. Here, the implementation of a secure long-term isolation procedure will be necessary.

6.7.3 Shift hand-overs

Shift changeovers can be one of the most vulnerable times for the P.T.W. system. Failure to pass on correct information has been the cause of many accidents. During shift hand-overs, proper planning is required to properly review and discuss information between two work shifts.

Tools used to communicate information include:

- Permit Log Book

- Permit Files

- Display Boards

- Computer Screen/Print Out

- Or a combination of any of the above items

6.7.4 Action in an emergency

The P.T.W. system should make provision for actions in an emergency. Normally, in this situation, the whole work is stopped in accordance with an instruction and time may not allow formal suspension of permits. Post-emergency actions include a re-assessment of work to ensure that conditions have not altered as a result of the emergency and that the permit remains valid. New assessment of working conditions and new permit will be required in the event of any change in working conditions.

6.7.5 Reviewing, monitoring and controlling the permit

Continuous monitoring of a P.T.W. system is required. This process should be performed by relevant personal in HSE Department/operational units/Repair and Maintenance Department, etc. The purpose of monitoring is to ensure that the conditions under which the permit was issued remain unaltered and that the precautions specified on the permit are being complied with. In the event of any change in working conditions, immediate action must be taken, problems shall be resolved and new permit must be issued.

6.8 Completion of work

6.8.1 Return of permit

On completion of work, the issued copies of the permit should be returned to the point of issue. The copies should then be signed off by the permit issuer and the supervisor of the work to indicate completion. Other personnel who have been aware of the work should also be informed and notified.

6.8.2 Site inspection

Before signing the permit, the permit issuer or his representative should conduct an inspection of the worksite to confirm that it has been left in a satisfactory condition. The person in charge of the work shall make a statement that the worksite has been left in a safe condition and the permit issuer shall sign the permit after conducting site inspection.

6.8.3 Cancellation of overrides

Where the override of process shutdown or fire and gas detection/protection systems has been necessary to allow work to proceed, these should be cancelled as part of the permit completion arrangements.

Overrides should be in place in the shortest practicable time and one should not necessarily wait until the work is completed.

Whenever the permit issuer is satisfied that such overrides are no longer required, he should authorize their cancellation and authorization. The cancellation of overrides should be indicated on the permit.

6.8.4 Return to service

There should be a formal procedure for returning equipment to service which has been subject to work under the P.T.W. system. The following items should be considered before returning to service:

- Work on the equipment has been completed.

- Facilities or equipment have been left in a safe condition and the permit issuer has verified this issue.

- All isolations/overrides pertaining to the unit or equipment have been removed/cancelled or the operational personnel are aware of the status of the remaining isolations/overrides.

- Relevant authorities shall formally declare their agreement with returning to service.

6.8.5 Logs/records

A system shall be designed for recording permits issued over a specified period. Such a system may consist of a permit log book itemizing issued permits or of permit copies being retained for the specified period.

Records are often retained for a 12-month period.

7. Appendices

- P.T.W. Inspection Checklist

- Checklist for the Review of P.T.W. Systems

- Hot Work Permit

- Cold Work Permit

- Isolation/Override (electrical/mechanical/instrumentation) Certificate

- Extended Period Isolation

- Joint Area Permit

- Joint Diving Permit

- De-isolation for Testing Certificate

- Certificate for Putting Safety and Emergency Systems out of Service

- Certificate for Repairing Safety and Emergency Systems

- Radiography Certificate

- Excavation and Trenching Certificate

- Scaffolding Certificate

- Confined Space Certificate

- TRIC Card

- Sample of Certificate of Permit Issuance

8. References

- Guideline On Permit to Work (P.T.W) system-IOGP

- Permit To Work System Manual – PDO

Appendix 1: Inspection checklist

The successful implementation of the P.T.W. system largely depends on the competence of the personnel responsible for authorizing the work, strict supervision and precision and care. Regular supervision and auditing is required to ensure operating at maximum effectiveness. The attached forms are given as guidance to individuals involved with such an audit. Straight yes/no answers may not be sufficient; therefore, it is recommended to provide thorough answers, if necessary.

Facility: ......................................................... Permit issuer: .......................................................

Facility manager: .......................................... Supervisor: ..................................................

Auditor: .............................................................. Date: ...................................................................

Description of work (including work location):

…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..…………………………………………………………………………………………………………..

Appendix 1: Inspection Checklist

| No. | Issue time | Valid until | Comments |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Permit No. |  |  |  |  |
| 2 | Date of issuance |  |  |  |  |
| 3 | Type of permit |  |  |  |  |
| 4 | Distribution and display Have permit copies been properly distributed, and where necessary is a permit prominently displayed? |  |  | Yes | No |
| 5 | Is the work description on the permit adequate (in terms of describing the work location, the equipment and the exact nature of the work)? If not, explain: |  |  |  |  |
| 6 | Validity a) Is the permit time and date clearly stated? b) Has the permit been revalidated, signed and dated? c) Are revalidations up to date? |  |  |  |  |
| 7 | Hazards a) Have all hazards been clearly identified? b) Are they directly applicable to the job being undertaken? |  |  |  |  |
| 8 | Precautions a) Have appropriate precautions been defined? b) Have other affected personnel outside the permit area been notified of the permit work? (If yes: have they signed the permit?) c) Have all precautions been implemented at the worksite? (If not: explain) |  |  |  |  |
| 9 | Gas Tests a) Have all gas tests been performed? b) Are performed tests valid for this period? c) Are portable gas monitors fully operable at worksite and calibrated? d) Can on-site personnel operate equipment? e) Have they been properly trained in its use? f) Has adequate periodic testing been carried out as appropriate? |  |  |  |  |
| 10 | Precautions Taken by the supervisor of the work a) Has the supervisor of the work briefed all relevant personnel? b) Have all the personnel read the permit thoroughly? c) Do all persons fully understand safety requirements and the precautions specified in the P.T.W? d) Have all safety requirements been observed? (E.g. using safety clothing, isolating equipment at breaks, etc.) If not: specify. |  |  |  |  |
| 11 | Isolation a) Are isolation certificates attached to the permit? b) Have all cross references been considered? c) Do certificates or attachments explain all isolation points in details? d) Are all isolations safe? e) Are all isolations tagged? f) If more than one task is performed on same isolation, has multiple lock/key system or other suitable control been used? Give details. |  |  |  |  |
| 12 | Precautions undertaken by permit issuer a) Has task been fully discussed with person carrying out the isolation? b) Has task been discussed with the supervisor? c) If more than one permit on equipment/system, have all appropriate cross references been made and all necessary personnel been made aware? d) Where tasks may impinge on other responsible persons/areas, have affected persons signed to acknowledge their awareness of the work? |  |  |  |  |
| 13 | Handover a) Has handover of permit been done between permit issuers at shift change? b) How has the above item been documented? c) Do the supervisors communicate their information during handovers? d) How is this being documented? |  |  |  |  |
| 14 | Work suspended/on hold/completed a) Has the site been left in a safe and tidy condition? b) In the case of incomplete work, are isolations secure? c) Is the permit issuer aware of the workplace status? d) Is the control room aware of the workplace status? |  |  |  |  |
| 15 | Training a) Have relevant personnel received training on P.T.W system? b) Is the type and frequency of trainings in accordance with the company policy? c) Is evidence of training and certificates readily available? d) Do the permit issuers hold “certificate cards”? e) Is the card still valid? |  |  |  |  |
| Summarize the overall audit process: ……………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………… Auditor’s full name: …………….. Signature: ………… Date: …………….. |  |  |  |  |  |

Appendix 2: Checklist for the Review of P.T.W. Systems

The purpose of this checklist is to help relevant personnel prepare a suitable P.T.W system. It helps people cover all essential points in a P.T.W system. If the answer to any of the questions below is “no”, the system may need to be reconsidered and changed.

| No. | Items | Yes | No |
| --- | --- | --- | --- |
| The system |  |  |  |
| 1 | Does the permit system cover all legal requirements applying to the site or facility? |  |  |
| 2 | Is the permit system recognized throughout the site as being essential for certain types of work? |  |  |
| 3 | Are various types of work, types of job or areas where permits must be used clearly defined and known to all beneficiaries? |  |  |
| 4 | Has the permit system been thoroughly explained to contractors, project managers, plan executors and their employees? |  |  |
| 5 | Has the permit issuer been clearly determined? |  |  |
| 6 | Is it clearly laid down how permits should be completed for specific jobs? |  |  |
| 7 | Is the permit system flexible enough to allow it to be applied to other potentially hazardous work, apart from that which may have been specifically identified when the system was established? |  |  |
| 8 | Is the issue of a permit by a person to themselves prevented? |  |  |
| 9 | Does the system provide both for the recipient to retain the permit and for a record of live permits and suspended permits to be maintained at the point of issue? |  |  |
| 10 | Does the system require a copy of the permit to be displayed at the workplace? |  |  |
| 11 | Does the system require the display of live and suspended permits, so that process operating staff can readily see the status of the operating unit? |  |  |
| 12 | Is there a set of properly documented isolation procedures for working on potentially dangerous equipment and does it provide for long-term isolation? |  |  |
| No. | Items | Yes | No |
| Training and competence |  |  |  |
| 1 | Is the permit system clearly covered during site safety induction training? |  |  |
| 2 | Are personnel who have special responsibilities under the permit system (e.g. issuing and isolating authorities) properly authorized and trained to undertake required duties? |  |  |
| 3 | Do the personnel have sufficient time to carry out their duties? |  |  |
| 4 | Does the system require assessment of competence of personnel before assigning responsibilities? |  |  |
| 5 | Is a record of training and assessment maintained? |  |  |
| 6 | Are contractors and project managers included in training programs? |  |  |
| 7 | Are individuals provided with written confirmation of successful completion of relevant training? Are these documents checked before appointments are made within the P.T.W system? |  |  |
| No. | Items | Yes | No |
| The permit |  |  |  |
| 1 | Is there a clear requirement for stopping the work, when new hazards arise or old hazards recur? |  |  |
| 2 | Does the permit contain clear rules about how the job should be controlled or abandoned in the event of an emergency? |  |  |
| 3 | Do permits clearly specify the type of job? |  |  |
| 4 | Do permits clearly specify to whom they are issued? |  |  |
| 5 | Does the system require potential hazards at the work site to be clearly identified and recorded on the permit? |  |  |
| 6 | Does the permit clearly specify the precautions to be taken by the issuing and performing authorities? |  |  |
| 7 | Do permits clearly specify the geographical area of the site? |  |  |
| 8 | Do the recipients have to sign the permit to show that they have read the permit and understood it? |  |  |
| 9 | Do permits clearly specify a time limit for expiry or renewal? |  |  |
| 10 | Does the permit include a hand-over mechanism for works extending beyond a shift or other work period including work which has been suspended? |  |  |
| 11 | Is a final signature required when the job is completed? |  |  |
| 12 | Is there a procedure to bring to the attention of the site manager tasks which require inhibiting safety devices (e.g. fire detectors) to ensure that contingency plans and precautions are in place? |  |  |
| No. | Items | Yes | No |
| Coordination |  |  |  |
| 1 | Are copies of permits issued for the same equipment/area kept and displayed together? |  |  |
| 2 | Is there a means of coordinating all work activities to ensure potential interactions are identified? |  |  |
| 3 | Is there provision on the permit form to cross-reference other relevant certificates and permits? |  |  |
| 4 | Is there a procedure to obtain the agreement of others who could be affected by the proposed work, before commencing it? |  |  |
| 5 | Where there are isolations common to more than one permit, is there a procedure to prevent the removal of isolation, before signing all permits? |  |  |
| No. | Items | Yes | No |
| Monitoring |  |  |  |
| 1 | Is there a system of spot checks to ensure that permits are being properly established and implemented? |  |  |
| 2 | Is there a procedure to report incidents, when performing a work under a permit? |  |  |
| 3 | Are audits carried out on the P.T.W system at least once a year, preferably by people not normally employed at that site? |  |  |

Appendix 3: Hot Work Permit Form

| Hot Work Permit Form code: Company: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Serial number: ................. Unit name / Section: ....... Appendix: ..... |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Description of work: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The exact workplace (the type and number of device): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Equipment/tools: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Working group/groups: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Agenda No.: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hazard identification |  | Process hazards: |  |  |  |  |  |  |  |  |  |  | Work-related hazards: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Workplace-related hazards: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | □ Chemical material: ....... □ Isolation □ Safety systems □ Flammable and explosive □ Toxic □ Hot material’s surface temperature: ........ □ Cold material’s surface temperature: .... □ Corrosive □ Pressure: □ Rotating equipment □ Loaded devices / pipelines |  |  |  |  |  |  |  |  |  |  | □ Electricity: .... □ Spark □ Automobile □ Direct flame or arc □ Static electricity □ Height: ... □ Flying particles □ Pressure test: ..... |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ Oxygen deficiency □ Severe wind □ Radioactivity □ H2S □ Rainfall □ Sound □ Confined space □ Dust □ Surface □ Ambient temperature: ... □ Slippery surface □ Access limitation □ Low light □ Adjacent operations: |  |  |  |  |  |  |  |  |  |  |  |  |
| Preparation |  | Requirements and precautionary measures |  |  |  |  |  |  |  |  |  |  |  | Requirement/Application |  |  |  |  |  |  |  | Done |  | Requirement/Application |  |  |  |  |  |  |  |  | Requirement/Application |  |  |  |  |  |  |  | Done |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |  |  |  |
|  |  | Valves are used to shut off the upstream flow. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Shutting electricity off |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The flow path is isolated using blocking plates. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Using tag out label |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Drained completely. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Using lock out system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Fully ventilated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Portable cables pass suitable paths. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Washing with: water □ steam □ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MSDS provisions are observed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Purge is neutralized using gas. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Radioactive materials are properly isolated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Preventing entry of sparks and molded materials into seams, gaps, wells and sewage (suitable cover). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Scaffolding and work platform are secure. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Cleaning combustible and flammable materials (12 m radius) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The presence of standby personnel: □ Operator □ Firefighter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Controlling fire alarm and extinguishing systems. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Welding machine is properly grounded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The ESD system No. ... is overridden as described below. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Has the TRIC been completed? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Instruction/procedure No.: …. □ Inspection agenda □ Engineering agenda □ Isolation list No. □ Confined space permit □ Excavation permit □ Vehicle entry permit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Other precautionary measures and inspections: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Precautionary measures |  | PPEs | General PPES |  |  |  |  |  |  | Eyes | □ Safety glasses □ Welding glasses □ Goggles |  |  |  | Hands |  |  |  | □ Leather □ Electricity Insulation □ Cloth □ PVC □ Anti-vibration □ Thermal insulation/fireproof □ Cold insulation □ Anti-Acid and anti-chemicals |  |  |  |  |  |  | Body |  | □ Leather apron □ Safety belt (harness) □ Life jacket □ Anti-acid and anti-chemical cloth |  |  |  | Respiratory system |  |  |  |  | □ Dust mask □ Full-face mask □ Half-face mask □ Airline □ SCBA |  |  |  |  |  |
|  |  | Emergency equipment | □ Fire extinguisher □ Fireproof blankets □ Rescue equipment □ Communication equipment □ Fire hose □ Foam system |  |  |  |  |  |  | Foot | □ Electrical insulation □ Safety boots |  |  |  |  |  |  |  | Ears |  |  | Earplug/earmuff |  |  | Other equipment and precautions |  |  |  |  |  |  |  |  |  |  | □ Danger tape and warning signs □Flashlight/explosion-proof lighting □ Non-sparking tools □ Personal gas meter |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | Face | □ Face shield |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: This permit will only be issued by authorized persons. These persons are responsible for the safe operation of the work as well as preparedness for the occurrence of any emergency. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Authorization of the work | Facilities/site |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | First authorization: facility/unit/shift manager |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | I have personally inspected all above items. I confirm the accuracy of the above items. The site is safe to perform the work and I have guided the person in charge of the work to the workplace. Name and signature |  |  |  |  |  |  |  |  |  |  |  |  |  | All workplace hazards have been identified, workers have been trained, the permit has been displayed properly and precautionary measures have been taken. Name and signature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Gas testing |  | At one time |  |  |  |  | Periodic | Continuous |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hour |  |  |  |  |  |  | Every..... hour |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | O2 |  |  |  |  |  |  | Every..... hour |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Toxic gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | □ %LEL |  |  | Inside the system / device / equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Inside the ambient |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Gas meter No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Tester’s license |  |  |  |  |  |  |  |  |  |  | No.: Name and signature: |  |  |  |  | No.: Name and signature: |  |  |  |  | No.: Name and signature: |  |  |  |  | No.: Name and signature: |  |  |  |  |  |  |  | No.: Name and signature: |  |  |  |  |  |  |  |
| Closing the permit | □ Work has been completed □ Temporary interruption has occurred and work has not been completed □ Work is ongoing, with a new permit. □ New permit No.: □ Permit has been cancelled due to: Date: Hour: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Actions taken |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Not applicable |  | Yes |  | No |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | All employees have left the workplace. All devices are installed in safe conditions. Mechanical/electrical barriers have been properly removed. All devices are posed in normal state. All problems have been properly resolved. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Person in charge of the work: Name and signature of the deliverer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Facility/unit/shift manager: Name and signature of the deliverer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Emergency telephone numbers: |  |  |  |  |  |  | Fire number: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Emergency department number: |  |  |  |  |  |  |  | Security number: |  |  |  |  |  |  |  |  |  |  |  |
| Distribution of copies |  |  |  |  |  |  | White copy: the facility/site manager |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yellow: Person in charge of the work Green: HSE Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Appendix 4: Cold Work Permit Form

| Cold Work Permit Form code: Company: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Serial number: ................. Unit name / Section: ....... Appendix: ..... |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Description of work: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The exact workplace (the type and number of device): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Equipment/tools: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Working group/groups: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Agenda No.: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hazard identification |  | Process hazards: |  |  |  |  |  |  |  |  |  |  | Work-related hazards: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Workplace-related hazards: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | □ Chemical material: ....... □ Isolation □ Safety systems □ Flammable and explosive □ Toxic □ Hot material’s surface temperature: ........ □ Cold material’s surface temperature: .... □ Corrosive □ Pressure: □ Rotating equipment □ Loaded devices / pipelines |  |  |  |  |  |  |  |  |  |  | □ Electricity: .... □ Spark □ Automobile □ Direct flame or arc □ Static electricity □ Height: ... □ Flying particles □ Pressure test: ..... |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | □ Oxygen deficiency □ Severe wind □ Radioactivity □ H2S □ Rainfall □ Sound □ Confined space □ Dust □ Surface □ Ambient temperature: ... □ Slippery surface □ Access limitation □ Low light □ Adjacent operations: |  |  |  |  |  |  |  |  |  |  |  |  |
| Preparation |  | Requirements and precautionary measures |  |  |  |  |  |  |  |  |  |  |  | Requirement/Application |  |  |  |  |  |  |  | Done |  | Requirement/Application |  |  |  |  |  |  |  |  | Requirement/Application |  |  |  |  |  |  |  | Done |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  | No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  | No |  |  |  |
|  |  | Valves are used to shut off the upstream flow. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Shutting electricity off |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The flow path is isolated using blocking plates. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Using tag out label |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Drained completely. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Using lock out system |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Fully ventilated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Portable cables pass suitable paths. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Washing with: water □ steam □ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MSDS provisions are observed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Purge is neutralized using gas. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Radioactive materials are properly isolated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Preventing entry of sparks and molded materials into seams, gaps, wells and sewage (suitable cover). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Scaffolding and work platform are secure. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Cleaning combustible and flammable materials (12 m radius) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | The presence of standby personnel: □ Operator □ Firefighter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Controlling fire alarm and extinguishing systems. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Welding machine is properly grounded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The ESD system No. ... is overridden as described below. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Has the TRIC been completed? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Instruction/procedure No.: …. □ Inspection agenda □ Engineering agenda □ Isolation list No. □ Confined space permit □ Excavation permit □ Vehicle entry permit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Other precautionary measures and inspections: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Precautionary measures |  | PPEs | General PPES |  |  |  |  |  |  | Eyes | □ Safety glasses □ Welding glasses □ Goggles |  |  |  | Hands |  |  |  | □ Leather □ Electricity Insulation □ Cloth □ PVC □ Anti-vibration □ Thermal insulation/fireproof □ Cold insulation □ Anti-Acid and anti-chemicals |  |  |  |  |  |  | Body |  | □ Leather apron □ Safety belt (harness) □ Life jacket □ Anti-acid and anti-chemical cloth |  |  |  | Respiratory system |  |  |  |  | □ Dust mask □ Full-face mask □ Half-face mask □ Airline □ SCBA |  |  |  |  |  |
|  |  | Emergency equipment | □ Fire extinguisher □ Fireproof blankets □ Rescue equipment □ Communication equipment □ Fire hose □ Foam system |  |  |  |  |  |  | Foot | □ Electrical insulation □ Safety boots |  |  |  |  |  |  |  | Ears |  |  | Earplug/earmuff |  |  | Other equipment and precautions |  |  |  |  |  |  |  |  |  |  | □ Danger tape and warning signs □Flashlight/explosion-proof lighting □ Non-sparking tools □ Personal gas meter |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | Face | □ Face shield |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: This permit will only be issued by authorized persons. These persons are responsible for the safe operation of the work as well as preparedness for the occurrence of any emergency. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Authorization of the work | Facilities/site |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | First authorization: facility/unit/shift manager |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | I have personally inspected all above items. I confirm the accuracy of the above items. The site is safe to perform the work and I have guided the person in charge of the work to the workplace. Name and signature |  |  |  |  |  |  |  |  |  |  |  |  |  | All workplace hazards have been identified, workers have been trained, the permit has been displayed properly and precautionary measures have been taken. Name and signature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Gas testing |  | At one time |  |  |  |  | Periodic | Continuous |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hour |  |  |  |  |  |  | Every..... hour |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | O2 |  |  |  |  |  |  | Every..... hour |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Toxic gas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | □ %LEL |  |  | Inside the system / device / equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Inside the ambient |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Gas meter No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Tester’s license |  |  |  |  |  |  |  |  |  |  | No.: Name and signature: |  |  |  |  | No.: Name and signature: |  |  |  |  | No.: Name and signature: |  |  |  |  | No.: Name and signature: |  |  |  |  |  |  |  | No.: Name and signature: |  |  |  |  |  |  |  |
| Closing the permit | □ Work has been completed □ Temporary interruption has occurred and work has not been completed □ Work is ongoing, with a new permit. □ New permit No.: □ Permit has been cancelled due to: Date: Hour: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Actions taken |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Not applicable |  | Yes |  | No |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | All employees have left the workplace. All devices are installed in safe conditions. Mechanical/electrical barriers have been properly removed. All devices are posed in normal state. All problems have been properly resolved. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Person in charge of the work: Name and signature of the deliverer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Facility/unit/shift manager: Name and signature of the deliverer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Emergency telephone numbers: |  |  |  |  |  |  | Fire number: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Emergency department number: |  |  |  |  |  |  |  | Security number: |  |  |  |  |  |  |  |  |  |  |  |
| Distribution of copies |  |  |  |  |  |  | White copy: the facility/site manager |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yellow: Person in charge of the work Green: HSE Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Appendix 5: Isolation/Override (electrical/mechanical/instrumentation) Certificate

| National Iranian Oil Company Isolation/Override (electrical/mechanical/instrumentation) Certificate Permit No.: ... Serial No.: ... |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Workplace: Hot work permit No.: ....... Cold work permit No.: …. |  |  |  |  |  |  |  |  |  |
| 1. Electrical Isolation: |  |  |  |  |  |  |  |  |  |
| Device No.: .... High voltage: ... Low voltage: … Device: … |  |  |  |  |  |  |  |  |  |
| A. Applicant (permit applicant or work supervisor): Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| B. Agreement of area manager (head of unit): Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| C. Isolation executor: Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| D. The HSE representative (no interference with other activities) Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| Isolation place | Place of switches |  | Place of fuses |  |  | Disconnecting power supply | Disconnecting devices |  | Other considerations |
| E) Isolation was carried out in accordance with relevant safety rules. Full name of Chief Electricity Officer / Authorized person: ... hour and date: … signature: … |  |  |  |  |  |  |  |  |  |
| Place of power keys |  |  |  |  |  |  |  |  |  |
|  |  | The switches are kept securely in order to isolate devices. |  |  |  |  |  |  |  |
| The first switch (the work supervisor) |  | Verifier: … |  | Date: … | Verifying return of switch: … |  |  | Date: … |  |
| The second switch (the Electricity Officer) |  | Verifier: … |  | Date: … | Verifying return of switch: … |  |  | Date: … |  |
| The third switch (the HSE Department) |  | Verifier: … |  | Date: … | Verifying return of switch: … |  |  | Date: … |  |
| Cancelation of Electrical Isolation: |  |  |  |  |  |  |  |  |  |
| A. Applicant (permit applicant or work supervisor): Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| B. Agreement of area manager (head of unit): Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| C. Isolation executor: Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| D. The HSE representative (no interference with other activities) Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |
| E. Electricity Officer (Cancelation of Electrical Isolation) Full name: ... Signature: ... Date: … |  |  |  |  |  |  |  |  |  |

| 1. Mechanical Isolation: |  |  |  |
| --- | --- | --- | --- |
| Device No.: .... Device: … Appendix: … |  |  |  |
| Isolation De-Isolation |  |  |  |
| A. Applicant (permit applicant or work supervisor): | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| B. Agreement of area manager (head of unit): | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| C. Isolation executor: | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| D. The HSE representative (no interference with other activities) | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| Blank; Spade; Closed; Open; Valve No.. | Blank; Spade; Closed; Open; Valve No.. |
| Isolation executor: Full name: ... Signature: ... Date: … Full name: ... Signature: ... Date: … |  |  |  |
| 3. Isolation of Safety and Emergency Systems: … Appendix: … |  |  |  |
| Isolation De-Isolation |  |  |  |
| A. Applicant (permit applicant or work supervisor): | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| B. Agreement of area manager (head of unit): | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| C. Isolation executor: | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| D. The HSE representative (no interference with other activities) | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| E. Isolation or De-Isolation was performed. Isolation executor: | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| And: confirmation of the Control Room Operator | Full name: ... Signature: ... Date: … | Full name: ... Signature: ... Date: … |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |

Appendix 6: Extended Period Isolation

| National Iranian Oil Company Serial Number: ... Extended Period Isolation (EPI) Control Sheet No.: … |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Isolation certificate No.: |  |  | Date: |  |  |  |
| Unit: |  |  | System: |  |  |  |
| Type (electrical/mechanical/instrumentation( |  |  | Place of EPI switch: |  |  |  |
| Reason for EPI: |  |  |  |  |  |  |
| Measures required: |  |  |  |  |  |  |
| Rev. No. |  |  |  |  |  |  |
| Manager of unit | Full name: ... |  |  | Signature: ... | Date: … |  |
| Electricity supervisor | Full name: ... |  |  | Signature: ... | Date: … |  |
| Facility supervisor | Full name: ... |  |  | Signature: ... | Date: … |  |
| HSE Representative | Full name: ... |  |  | Signature: ... | Date: … |  |

Appendix 7: Joint Area Permit

| National Iranian Oil Company |  | Joint Area Permit |  | Permit No.: |  |  | Serial Number: |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Fixed facilities (platform(: | Adjacent facilities (platform/drilling rig) |  | Location: |  | Device No.: | Classification of areas: O-1; O-2; 0: without danger |  |
| 1. Applicant: Full name: ... Signature: … |  |  | Work schedule: Start time: ... Date: ... Ending time: ... Date: ... |  |  |  |  |
| 2. Work description and reasons for request: …………………………………………………….. |  |  |  |  |  |  |  |
| 3. Person in charge of the work: Full name: ... Post: … |  |  |  |  |  |  |  |
| 4. Procurement/precautionary measures in fixed facilities Tick; Certificate No.. Electrical isolation. Safety/Emergency. Mechanical isolation. Special precautions. Required checklist. | 4. Procurement/precautionary measures in Adjacent facilities: ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………… |  |  |  |
| 6. Precautionary statements and checklists are correct. The work can be done at the relevant shift, upon signing the permit. Start time: ... Date: ... Ending time: ... Date: ... Full name: … Signature (Area Manager): … Full name: … Signature (Manager of Fixed Facilities): … Full name: … Signature (Manager of Adjacent Facilities): … |  |  |  | 7. HSE Representative: All possible interfering permits have been stopped. Work can be performed after taking the precautions mentioned in section 4. Full name: ... Signature: … Time: … Date: … |  |  |  |
| 8. Authorization (Area Manager): Precautionary measures mentioned in section 4 have been completed. Work can be done by agreement of the site manager. Full name: ... Signature: … … Date: … |  |  |  |  |  |  |  |
| 9. Reception: Person in charge of the work in the day shift: Full name: ... Signature: … Time: … Date: … Person in charge of the work in the night shift: Full name: ... Signature: … Time: … Date: … |  |  |  |  |  |  |  |
| The site manager confirms the start of the work at the beginning of each shift. The person in charge of the work confirms the end of the work at the end of each shift. |  |  |  |  |  |  |  |
| Area Manager. Person in charge of the work. Area Manager. Person in charge of the work. |
| 10. Permit Cancellation: The person in charge of the work: The work has been completed. The workplace and equipment are left in a safe status. Full name: ... Signature: … Time: … Date: … Area Manager: Cancellation of Permit, Isolation is done perfectly. Full name: ... Signature: … Time: … Date: … |  |  |  | 11. The HSE Representative: The work has not been completed. The work continues under the new permit No.: ... The isolation certificate number remains the same (No.: …). Full name: ... Signature: … Time: … Date: … |  |  |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |  |  |  |  |

Appendix 8: Joint Diving Permit

| National Iranian Oil Company |  | Joint Diving Permit |  | Permit No.: | Serial Number: |
| --- | --- | --- | --- | --- | --- |
| Fixed facilities (platform(: | Diving Support Vessel: |  | Location: |  |  |
| 1. Applicant: Full name: ... Signature: … |  |  | Work schedule: Start time: ... Date: ... Ending time: ... Date: ... |  |  |
| 2. Work description and reasons for request: …………………………………………………….. |  |  |  |  |  |
| 3. Person in charge of the work: Full name: ... Post: … |  |  |  |  |  |
| 4. Procurement/precautionary measures in the main platform Tick; Certificate No.. Electrical isolation. Safety/Emergency. Mechanical isolation. Special precautions. Required checklist. | 4. Procurement/precautionary measures in the diving support vessel: ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………… |  |
| 6. Precautionary statements and checklists are correct. The work can be done at the relevant shift, upon signing the permit. Start time: ... Date: ... Ending time: ... Date: ... Full name: … Signature (Head of Operation Unit): … Full name: … Signature (Platform Manager): … Full name: … Signature (Manager of diving support vessel): … |  |  |  | 7. HSE Representative: All possible interfering permits have been stopped. Work can be performed after taking the precautions mentioned in section 4. Full name: ... Signature: … Time: … Date: … |  |
| 8. Authorization (Head of Operation Unit): Precautionary measures mentioned in section 4 have been completed. Work can be done by agreement of the site manager. Full name: ... Signature: … … Date: … |  |  |  |  |  |
| 9. Reception by Person in charge of the work (Diving Supervisor): Person in charge of the work in the day shift: Full name: ... Signature: … Time: … Date: … Person in charge of the work in the night shift: Full name: ... Signature: … Time: … Date: … |  |  |  |  |  |
| The person in charge of the work confirms the start and termination of the work. |  |  |  |  |  |
| From. Date. To. |
| 10. Permit Cancellation: The person in charge of the work (Diving Supervisor): The work has been completed. The workplace and equipment are left in a safe status. Full name: ... Signature: … Time: … Date: … Head of Operation Unit: Cancellation of Permit, Isolation is done perfectly. Full name: ... Signature: … Time: … Date: … |  |  |  | 11. The HSE Representative: The work has not been completed. The work continues under the new permit No.: ... The isolation certificate number remains the same (No.: …). Full name: ... Signature: … Time: … Date: … |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |  |  |

Appendix 9: De-isolation for Testing Certificate

| Serial Number: | Permit No.: | De-isolation for Testing Certificate |  | National Iranian Oil Company |
| --- | --- | --- | --- | --- |
| Device/Equipment: | Isolation Authorization No.: |  | Location: |  |
| 1. Application: ………………………………………………………………………………………………………………………… ……………………………………………………………. |  |  |  |  |
| Describing the process (Test/Isolation/ De-Isolation): ………………………………………………………………………………………………………………………… ……………………………………………………………. |  |  |  |  |
| De-Isolation Request for testing (by person in charge of the work): Full name: … Time: … Date: … Signature: … |  |  |  |  |
| 2. Authorization: ………………………………………………………………………………………………………………… ……………………………………………………………………… |  |  |  |  |
| Isolation/De-Isolation Executor: Full name: … Time: … Date: … Signature: … |  |  |  |  |
| Authorization by Area Manager: Full name: … Time: … Date: … Signature: … |  |  |  |  |
| HSE Representative: The process does not interfere with other activities. Full name: … Time: … Date: … Signature: … |  |  |  |  |
| 3. Completing Isolation/De-Isolation Test Number; De-Isolation; Isolation. Completing De-Isolation; Completing Isolation. Full name; Signature; Time; Date; Full name; Signature; Time; Date. Test 1. Test 2. Test 3. Test 4. |
| 4. Cancellation: The test was completed and the system was left in a safe status. (By Isolation/De-Isolation Executor) Full name: … Time: … Date: … Signature: … |  |  |  |  |
| (Authorization by Area Manager): Isolation was cancelled. Full name: … Time: … Date: … Signature: … |  |  |  |  |
| HSE Representative: Isolation was cancelled and previous isolations returned to their normal states. Full name: … Time: … Date: … Signature: … |  |  |  |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |  |

Appendix 10: Certificate for Putting Safety and Emergency Systems out of Service

| National Iranian Oil Company Authorization Number: … Serial Number: … Certificate for Putting Safety and Emergency Systems out of Service |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| System |  |  | UV |  |  | IR |  |  |  | Gas Detection |  |  |  | Smoke/Heat |  |  | Firewater |  |  |  |
| Area of Detectors/ List |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Permit No. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| De-activation |  |  |  |  |  |  |  |  |  |  | Activation |  |  |  |  |  |  |  |  |  |
| Full name | Date | Time |  |  | Control Room Operator |  | Signature of person in charge of the work |  | Signature of HSE Representative |  | Full name |  | Date |  | Time | Control Room Operator |  | Signature of person in charge of the work |  | Signature of HSE Representative |
| All the above items were brought into service. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Control Room Operator: Full name: ... Signature: … Date: … |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Person in charge of the work: Full name: ... Signature: … Date: … |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Appendix 11: Certificate for Repairing Safety and Emergency Systems

| National Iranian Oil Company | Authorization Number: … |  | Serial Number: … |
| --- | --- | --- | --- |
| Certificate for Repairing Safety and Emergency Systems |  |  |  |
| Isolation area/system |  | Permit No.: … |  |
| Note: 1. The control room operator should be aware of all inhibitions/isolations. At least 50% of detectors in each circuit should be in service. 2. This document is only valid for the person who is allowed to perform inhibitions/isolations. It is not transferable. 3. The person in charge of the work is authorized to perform inhibitions/isolations. 4. The work is performed only in one area and in one working time period. |  |  |  |
| 1. Authorization |  |  |  |
| Inhibitions/isolations executor (person in charge of the work): Full name: … Time: … Date: … Signature: … |  |  |  |
| Authorization by Area Manager: Full name: … Time: … Date: … Signature: … |  |  |  |
| HSE Representative: Inhibitions/isolations do not interfere with other activities. Full name: … Time: … Date: … Signature: … |  |  |  |
| Inhibit/isolation off; Inhibit/isolation on; Detector/Valve/ Equipment. Type; Number; Loop; Time; Date; Signature of person in charge of the work/Control Room Operator; Time; Date; Signature of person in charge of the work/Control Room Operator. |
| 2. Completion of work: All Inhibitions/isolations are removed. Control Room Operator: Full name: … Time: … Date: … Signature: … |  |  |  |
| Person in charge of the work: Full name: … Time: … Date: … Signature: … |  |  |  |
| 3. HSE Representative: Isolation was cancelled and previous isolations returned to their normal states. Full name: … Time: … Date: … Signature: … |  |  |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |

Appendix 12: Radiography Certificate

| National Iranian Oil Company Radiography Certificate Permit No.: … Serial Number: … |  |  |  |
| --- | --- | --- | --- |
| Location: … Equipment/Pipelines: …. Term of validity: From: … To: … |  |  |  |
| 1. Conditions inspected by the Supervisor of the Radiography Team | Yes | No | If no, give reasons |
| 1.1 Has the work area been enclosed by safety tapes and warning lights? |  |  |  |
| 1.2 Is the leakage of radioactive source within acceptable limits? |  |  |  |
| 1.3 Does the radiation detector device work in full health? |  |  |  |
| 1.4 Are radiographers equipped with required PPEs? |  |  |  |
| 1.5 1-5 Has the HSE Department been informed about the desired work? |  |  |  |
| I have personally inspected all the above items and radiography is permitted. Supervisor of the Radiography Team: Full name: … Signature: … |  |  |  |
| 2. Conditions inspected by the Area Manager | Yes | No | If no, give reasons |
| 2.1 All devices have been fully emptied and, if necessary, washed with steam. |  |  |  |
| 2.2 All suspicious areas where steam, oil or gas may enter have been inspected and sealed. |  |  |  |
| 2.3 All items that may jeopardize the health of radiologists have been addressed. |  |  |  |
| 2.4 All people have departed the area. |  |  |  |
| Recommendations: |  |  |  |
| I have personally inspected all the above items. The site is completely safe for the work and the operational personnel are aware of the operation. Area Manager: Full name: … Signature: … Date: … |  |  |  |
| 3. HSE Representative: There is no interference with other activities. Full name: … Signature: … Date: … |  |  |  |
| 4. Termination of work: The above work was completed at ........................ and the radioactive source was transferred to a safe place. Supervisor of the Radiography Team: Full name: … Signature: … Area Manager: Full name: … Signature: … |  |  |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |

Appendix 13: Excavation and Trenching Certificate

| National Iranian Oil Company Authorization Number: … Serial Number: … Excavation and Trenching Certificate |  |  |  |
| --- | --- | --- | --- |
| Location: … Rough Sketch No. (By Engineering Department): … |  |  |  |
| 1. The safety requirements inspected by the Area Manager or the person in charge of the work | Yes | No | If no, give reasons |
| 1.1 Have electric cables/instrumentation/underground pipes etc. been specified in the attachment of the document (second page). Have relevant departments described needed precautionary measures? |  |  |  |
| 1.2 Is it necessary to construct a detour road? |  |  |  |
| 1.3 Has the work area been equipped with traffic signs, safety tapes and warning lights? |  |  |  |
| 1.4 Are there adequate fences and handrails available in the site? |  |  |  |
| 1.5 Is there a suitable ladder available for staff to access the ground? |  |  |  |
| 1.6 This work may jeopardize other activities. Have such activities been addressed? |  |  |  |
| 1.7 Are there necessary tools to prevent the collapse of trenches? |  |  |  |
| 2. Area Manager: All preventive measures have been fully and properly taken. Full name: … Signature: … Date: … |  |  |  |
| 3. Necessary precautions |  |  |  |
| Telecommunication manager: Full name: … Signature: … Date: … |  |  |  |
| Electricity manager: Full name: … Signature: … Date: … |  |  |  |
| Pipeline (oil and water) manager: Full name: … Signature: … Date: … |  |  |  |
| 4. HSE Representative: There is no interference with other activities. Full name: … Signature: … Date: … |  |  |  |
| 5. Person in charge of the work: I have personally inspected all the above items. The site is completely safe for the work. Full name: … Signature: … Date: … |  |  |  |
| 6. Cleaning: I hereby declare that all necessary works have been completed (or suspended). All my personnel have left the site and all equipment and tools have been removed. Person in charge of the work: Full name: … Signature: … Date: |  |  |  |
| 6. Cancellation of Certificate: Cancellation on the request of the person in charge of the work/applicant: the work is complete: □ Yes □ No Full name: … Signature: …; The person in charge of the work/applicant. |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |
| Considerations: The person in charge of the work and the site manager shall observe the following issues: 1. They shall fully study and implement the trenching and excavation rules and those related to working in the vicinity of high-voltage lines and shall observe the implementation of safely procedures. 2. They shall take into account all precautionary measures specified by authorities of the relevant units. 3. P & ID drawings should be attached to the permit. |  |  |  |
| Rough Sketch and other comments: |  |  |  |

Appendix 14: Scaffolding Certificate

| National Iranian Oil Company | Scaffolding Certificate | Authorization No.: … | Serial Number: … |
| --- | --- | --- | --- |
| 1. Scaffolding: Full name: … Location: … |  |  |  |
| Precautionary measures: |  |  |  |
| Person in charge of the work: Full name: … Signature: … Date: |  |  |  |
| Agreement of Area Manager: Full name: … Signature: … Date: |  |  |  |
| HSE Representative: There is no interference with other activities. Full name: … Signature: … Date: … |  |  |  |
| 2. Verification of Certificate The site manager confirms the start of the work at the beginning of each shift. The person in charge of the work confirms the end of the work at the end of each shift. Site Manager. Person in charge of the work. Site Manager. Person in charge of the work. |
| 3. Completing the scaffold Authorized person: The scaffold was completed in accordance with safety regulations. Full name: … Signature: … Date: …. |
| 4. Inspection: Periodic inspections: (Inspected by an authorized person( Date; Results; Full name; Signature. |
| 5. Making required changes Comments. Person who requests the change; Full name: …; Signature: …; Date: …; Time: …. Completer; Full name: …; Signature: …; Date: …; Time: …. The change was made (Site Manager); Full name: …; Signature: …; Date: …; Time: …. |
| 3. Dismantling the scaffold Comments. Person who requests dismantling; Full name: …; Signature: …; Date: …; Time: …. There is no interference with other activities (HSE Representative); Full name: …; Signature: …; Date: …; Time: …. The scaffold was dismantled (Person in charge of the work); Full name: …; Signature: …; Date: …; Time: …. |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |

Appendix 15: Confined Space Entry Certificate

| National Iranian Oil Company Authorization No.: … Serial Number: … Confined Space Entry Certificate |  |  |  |  |
| --- | --- | --- | --- | --- |
| 1. Work Description: ………………………………………………………………………………………………………… |  |  |  |  |
| 2. Position: Location: … Device No.: … Permit No.: … |  |  |  |  |
| 3. Preventive measures: The following items are inspected by the Area Manager (or the head of the unit or shift supervisor( |  | Yes | No | If no, give reasons |
| 3.1 All devices have been fully emptied and, if necessary, washed with steam. |  |  |  |  |
| 3.2 The device is isolated from electrical and mechanical sources? Isolation No.: |  |  |  |  |
| 3.3 A simultaneous work is being performed in the confined space. (interference) |  |  |  |  |
| 3.4 Enough lighting and ventilation are provided. |  |  |  |  |
| 3.5 Enough ventilation is provided. |  |  |  |  |
| 3.6 The standby person is aware of the details of the work. |  |  |  |  |
| 3.7 The air inside the device is continuously tested for gases. |  |  |  |  |
| 3.8 The rescue plan is prepared and relevant personnel are aware of it. |  |  |  |  |
| 3.9 Rescue equipment such as safety belts, lanyard and respiratory capsule are available. |  |  |  |  |
| 4. Validity of certificate: All the above items were inspected. Entrance into the confined space is authorized, after confirming the items. |  |  |  |  |
| Area Manager: The safety of the confined space is confirmed. Validity Term: From: … To: … Date: … Full name: … Signature: … |  |  |  |  |
| HSE Representative: There is no interference with other activities. Full name: … Signature: … Date: … |  |  |  |  |
| Person in charge of the work: I have personally inspected all above items and confirm the safety of the work. Full name: … Signature: … Date: … The above items are inspected by the Area Manager for each task.; The Arrival Time/Exit Time and the Number of Personnel are recorded in this section.. Area Manager; Arrival Time. Date and Time; Exit Time. Executor; Number of Personnel. |
| 5. Cancellation of Certificate: Cancellation on the request of the person in charge of the work/applicant: the work is complete: □ Yes □ No |  |  |  |  |
| Applicant of the work/Person in charge of the work | Full name: … Signature: … |  |  |  |
| Area Manager /Head of the Unit | Full name: … Signature: … |  |  |  |
| First copy: Control Room Second copy: Workplace Third copy: HSE Department |  |  |  |  |

Appendix 16: TRIC Card

| National Iranian Oil Company TRIC Card Permit No.: … Serial Number: … |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location: … Person in charge of the work: Working Group names: 1. 2. 3. 4. 5. 6. 7. 8. |  |  |  |  |  |  |  |
| Hazard/Risk Identification |  |  |  | In this case, the work may be hazardous and some precautionary measures should be taken. Remember, everyone is responsible for the following items: - Using the right tool - Awareness of existing hazards and possible changes in the work - Using suitable PPEs - Full awareness of permit conditions |  |  |  |
| 1. Will the work include the following items? |  |  | Yes/No |  |  |  |  |
| 1-1 Does the work necessitate using lifting equipment? |  |  |  |  |  |  |  |
| 1-1-1 Is the work related to lifting objects? |  |  |  |  |  |  |  |
| 1-1-2 Is it necessary to use a separate program or diagram for lifting objects? |  |  |  |  |  |  |  |
| 1-2 Is the workplace noisy? |  |  |  |  |  |  |  |
| 1-3 Is there the possibility of pipeline disruption or hydrocarbon release? 1-4 Will the incident negatively affect the environment? 1-5. Are cargos/objects/people carried by hand? |  |  |  | Hazard/Risk Management |  |  |  |
|  |  |  |  | 2. Will all personnel respond to the following questions? |  |  |  |
|  |  |  |  | 2-1 Have all major work-related hazards been identified? |  |  | Yes/No |
| 1-6 Is the work being performed in the vicinity of possibly moving objects? |  |  |  | 2-1 Has any risk management tool been specified? |  |  |  |
| 1-7 Is the work being performed in a poor-light and confined space? |  |  |  | 2-3 Have all the people responsible for using the control tools been identified? Is there any control tool available? |  |  |  |
| 1-8 Is the work being performed at height? |  |  |  | 2-4 Do the above people use a common communication method? |  |  |  |
| 1-9 Is there a possibility of slipping or falling? |  |  |  | 2-5 Is everyone aware of the nature of the work? |  |  |  |
| 1-10 Are portable electric appliances being used? |  |  |  | 2-6 Is everyone aware of what other personnel do at the workplace? |  |  |  |
| 1-11 Are pressurized equipment or fittings being used? |  |  |  | 2-7 Does everyone know that any change in the work should be communicated to the relevant authority? |  |  |  |
| 1-12 Are hazardous industrial materials being used? |  |  |  | If the answer to one of the above questions is “no”, the safety of individuals is at risk. |  |  |  |
| 1-13- Are there new unauthorized people in the workplace? |  |  |  | To make sure that everyone has fully understood the above points, the person in charge of the work must asks questions. |  |  |  |
| 1-14 Are there any potentially hazardous equipment? |  |  |  |  |  |  |  |
| Risk Control: An overview of the major risk control points raised in group discussions |  |  |  |  |  |  |  |
| The type of work Steps | Hazards Work-related hazards and their effects | Control Risk reduction and control procedures |  |  | Responsibilities Risk control officer | Are there control tools available in the workplace? Yes/No |  |

Appendix 17: Sample of Certificate of Permit Issuance

| Validity Term: One Year | Code: … Number: … Date: … | Permit To Work | Attach photo |
| --- | --- | --- | --- |
|  | Hereby, it is certified that Mr. ... ID Card No. …, working in ... (Company) has successfully completed the Hot/Cold Work training program and is authorized to issue relevant permits. Head of the Safety Department |  |  |

No. 17, Yaghma Alley, Jomhuri Eslami Avenue, Tehran.

Tel. 66726016	Fax 66709723	SMS 10007615

HSEE@NIOC.IR	HTTP://HSE.NIOC.IR